## INSTRUCTIONS
INSTRUCTIONS
On the CHECKSHEET worksheet, fill in the site name, address, contact name, phone number and account manager info.
Find the equipment you need checksheets for on the EQCODES worksheet.
Copy and paste the equipment "Description(s)" from the EQCODES worksheet to the first column of the UNIT LIST worksheet, below the header "Description." DO NOT put the "Type" information in this column (ex., use AIR CONDITIONER, not AC). DO NOT leave blank cells between multiple descriptions.
Use the "Season" column only if you DO NOT need all seasons. Put the season(s) you need in that column, next to the respective equipment type. If you need three seaons, you will need to list each one separately, and the description must be in the adjacent cell in the first column. See the example below.
The following will create checkeets for an Air Conditioner for all seasons and checksheets for an Exhaust Fan for Winter and Summer only.
Description | Season
AIR CONDITIONER
EXHAUST FAN | Winter
EXHAUST FAN | Summer
NOTE: The characters in the UNIT LIST table must match the characters in the CHECKSHEET table. Extra spaces or misspellings will create unwanted results.
Return to the CHECKSHEET worksheet. Highlight any cell below the heading row.
From the "Data" menu, select "Filter," then "Advanced Filter."
DO NOT change the information in the "List range."
Using your mouse, place your cursor in the "Criteria range." Click on the UNIT LIST worksheet tab at the bottom of the Excel window. Select the heading row and all filled cells below it. Release the mouse and press <Enter>. When selecting the cells on the UNIT LIST, it will loooking something like this:
Description | Season
AIR CONDITIONER
EXHAUST FAN | Winter
EXHAUST FAN | Summer
On the CHECKSHEET worksheet, Excel will hide all the rows that do not match the criteria set in the table on the UNIT LIST.
Format the sheet to print as you would like it to appear. Insert page breaks, lengthen rows, or bold and highlight items.
NOTE: The form may be too wide to print on one page. Do a print preview to be sure. If the last column spills over to another page, go to "Page Setup" on the "File" menu and adjust the percentage scaling until it fits the width of one page.
TROUBLESHOOTING
After selecting the criteria range and pressing <Enter>, Excel returned to the CHECKSHEET worksheet, but there was nothing listed below the heading row.
Press <Page Up>. The top of the form is frozen. The checksheet information is probalby further up on the page.
If this does not fix the problem, the characters in the UNIT LIST table probably do not exactly match the chacters in the CHECKSHEET table. Check for extra spaces and misspellings.

## CHECKSHEET
Maintenance Tasks - DATA AIRE COMPUTER ROOM
Site: | City Hall, 33325 8th Ave S. Federal Way, WA 98003
Type | Description | Season | Checksheet Data
AC | AIR CONDITIONER | FALL | [ ] CHECK BELTS
AC | AIR CONDITIONER | FALL | [ ] CHECK PULLEY ALIGNMENT
AC | AIR CONDITIONER | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
AC | AIR CONDITIONER | FALL | [ ] ADD PAN TABS
AC | AIR CONDITIONER | FALL | [ ] CHECK UNUSUAL VIBRATION/NOISE
AC | AIR CONDITIONER | FALL | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
AC | AIR CONDITIONER | FALL | [ ] CHECK SUPPLY VOLTAGE
AC | AIR CONDITIONER | FALL | [ ] CHECK MOTOR AMPS
AC | AIR CONDITIONER | FALL | [ ] CHECK ECONOMIZER OPERATION
AC | AIR CONDITIONER | FALL | [ ] CHECK RELIEF DAMPERS
AC | AIR CONDITIONER | FALL | [ ] CHECK CONTROL SET POINTS
AC | AIR CONDITIONER | FALL | [ ] CHECK CRANKCASE HEATER
AC | AIR CONDITIONER | FALL | [ ] CHECK OIL LEVEL
AC | AIR CONDITIONER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
AC | AIR CONDITIONER | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
AC | AIR CONDITIONER | FALL | [ ] CHECK INDOOR COIL
AC | AIR CONDITIONER | FALL | TEMPERATURE DROP_________DEG F
AC | AIR CONDITIONER | FALL | [ ] CHECK COMPRESSOR DISCHARGE
AC | AIR CONDITIONER | FALL | TEMPERATURE_________DEG F
AC | AIR CONDITIONER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
AC | AIR CONDITIONER | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
AC | AIR CONDITIONER | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
AC | AIR CONDITIONER | FALL | [ ] CHECK PULLEY WEAR
AC | AIR CONDITIONER | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
AC | AIR CONDITIONER | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
AC | AIR CONDITIONER | FALL | BINDING AND LUBE
AC | AIR CONDITIONER | FALL | [ ] CHECK FRESH AIR SCREENS
AC | AIR CONDITIONER | FALL | ELECTRIC HEAT: (IF EQUIPPED)
AC | AIR CONDITIONER | FALL | [ ] CHECK AMP DRAW
AC | AIR CONDITIONER | FALL | [ ] CHECK CONTACTOR POINTS
AC | AIR CONDITIONER | FALL | [ ] CHECK SEQUENCER OPERATION
AC | AIR CONDITIONER | FALL | [ ] CHECK TEMPERATURE RISE
AC | AIR CONDITIONER | FALL | GAS HEAT: (IF EQUIPPED)
AC | AIR CONDITIONER | FALL | [ ] CHECK TEMPERATURE RISE
AC | AIR CONDITIONER | FALL | [ ] CHECK SEQUENCER OPERATION
AC | AIR CONDITIONER | FALL | [ ] CHECK FAN SWITCH
AC | AIR CONDITIONER | FALL | [ ] VISUAL INSPECTION OF HEAT EXCHANGERS AND
AC | AIR CONDITIONER | FALL | VISUAL CHECK OF FLUE
AC | AIR CONDITIONER | FALL | [ ] CHECK PILOT SETTING
AC | AIR CONDITIONER | FALL | [ ] CHECK MAIN LINE GAS PRESSURE
AC | AIR CONDITIONER | FALL | [ ] CHECK MANIFOLD GAS PRESSURE
AC | AIR CONDITIONER | FALL | [ ] CLEAN COMBUSTION BLOWER WHEEL
AC | AIR CONDITIONER | FALL | [ ] OIL COMBUSTION BLOWER MOTOR
AC | AIR CONDITIONER | FALL | [ ] CLEAN AND ADJUST IGNITOR
AC | AIR CONDITIONER | FALL | [ ] VISUALLY CHECK HEAT EXCHANGER FOR CRACKS
AC | AIR CONDITIONER | WINTER | [ ] CHECK BELTS
AC | AIR CONDITIONER | WINTER | [ ] CHECK PULLEY ALIGNMENT
AC | AIR CONDITIONER | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
AC | AIR CONDITIONER | WINTER | [ ] ADD PAN TABS
AC | AIR CONDITIONER | WINTER | [ ] CHECK UNUSUAL VIBRATION/NOISE
AC | AIR CONDITIONER | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
AC | AIR CONDITIONER | WINTER | [ ] CHECK SUPPLY VOLTAGE
AC | AIR CONDITIONER | WINTER | [ ] CHECK MOTOR AMPS
AC | AIR CONDITIONER | WINTER | [ ] CHECK ECONOMIZER OPERATION
AC | AIR CONDITIONER | WINTER | [ ] CHECK RELIEF DAMPERS
AC | AIR CONDITIONER | WINTER | [ ] CHECK CONTROL SET POINTS
AC | AIR CONDITIONER | WINTER | [ ] CHECK CRANKCASE HEATER
AC | AIR CONDITIONER | WINTER | [ ] CHECK OIL LEVEL
AC | AIR CONDITIONER | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
AC | AIR CONDITIONER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
AC | AIR CONDITIONER | WINTER | [ ] CHECK FRESH AIR INTAKE SCREENS
AC | AIR CONDITIONER | WINTER | ELECTRIC HEAT: (IF EQUIPPED)
AC | AIR CONDITIONER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
AC | AIR CONDITIONER | WINTER
AC | AIR CONDITIONER | WINTER | GAS HEAT: (IF EQUIPPED)
AC | AIR CONDITIONER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
AC | AIR CONDITIONER | SPRING | [ ] CHECK BELTS
AC | AIR CONDITIONER | SPRING | [ ] CHECK PULLEY ALIGNMENT
AC | AIR CONDITIONER | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
AC | AIR CONDITIONER | SPRING | [ ] ADD PAN TABS
AC | AIR CONDITIONER | SPRING | [ ] CHECK UNUSUAL VIBRATION/NOISE
AC | AIR CONDITIONER | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
AC | AIR CONDITIONER | SPRING | [ ] CHECK SUPPLY VOLTAGE
AC | AIR CONDITIONER | SPRING | [ ] CHECK MOTOR AMPS
AC | AIR CONDITIONER | SPRING | [ ] CHECK ECONOMIZER OPERATION
AC | AIR CONDITIONER | SPRING | [ ] CHECK RELIEF DAMPERS
AC | AIR CONDITIONER | SPRING | [ ] CHECK CONTROL SET POINTS
AC | AIR CONDITIONER | SPRING | [ ] CHECK CRANKCASE HEATER
AC | AIR CONDITIONER | SPRING | [ ] CHECK OIL LEVEL
AC | AIR CONDITIONER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
AC | AIR CONDITIONER | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
AC | AIR CONDITIONER | SPRING | [ ] OUTSIDE AIR TEMPERATURE______DEG.F.
AC | AIR CONDITIONER | SPRING | [ ] CHECK INDOOR COIL
AC | AIR CONDITIONER | SPRING | TEMPERATURE DROP_______DEG F
AC | AIR CONDITIONER | SPRING | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE______DEG F
AC | AIR CONDITIONER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
AC | AIR CONDITIONER | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
AC | AIR CONDITIONER | SPRING | [ ] CHECK COMPRESSOR SUCTION LINE TEMP._____DEG.F.
AC | AIR CONDITIONER | SPRING | [ ] CHECK SUB COOLING____________DEG. F.
AC | AIR CONDITIONER | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT AND BULB
AC | AIR CONDITIONER | SPRING | [ ] CHECK CAPACITY CONTROLS
AC | AIR CONDITIONER | SPRING | [ ] CHECK OPERATING CONTROLS PRESSURE SETTING
AC | AIR CONDITIONER | SPRING | [ ] CHECK SAFETIES
AC | AIR CONDITIONER | SPRING | [ ] CHECK OPERATING PRESSURES HP______LP________
AC | AIR CONDITIONER | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
AC | AIR CONDITIONER | SPRING | [ ] CHECK CONTACTOR POINTS
AC | AIR CONDITIONER | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
AC | AIR CONDITIONER | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
AC | AIR CONDITIONER | SPRING | [ ] LUBE BLOWER MOTOR
AC | AIR CONDITIONER | SPRING | [ ] CHECK OUTDOOR FAN BLADES/SUPPORTS
AC | AIR CONDITIONER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
AC | AIR CONDITIONER | SPRING | [ ] CHECK FRESH AIR INTAKE SCREENS
AC | AIR CONDITIONER | SPRING | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION IF APPLICAB
AC | AIR CONDITIONER | SPRING | FOR MORE THAN ONE UNIT AND/OR ONE SYSTEM LIST
AC | AIR CONDITIONER | SPRING | TEMPERATURES AND PRESSURES BELOW
AC | AIR CONDITIONER | SUMMER | [ ] CHECK BELTS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK PULLEY ALIGNMENT
AC | AIR CONDITIONER | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
AC | AIR CONDITIONER | SUMMER | [ ] ADD PAN TABS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK UNUSUAL VIBRATION/NOISE
AC | AIR CONDITIONER | SUMMER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
AC | AIR CONDITIONER | SUMMER | [ ] CHECK SUPPLY VOLTAGE
AC | AIR CONDITIONER | SUMMER | [ ] CHECK MOTOR AMPS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK ECONOMIZER OPERATION
AC | AIR CONDITIONER | SUMMER | [ ] CHECK RELIEF DAMPERS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK CONTROL SET POINTS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK CRANKCASE HEATER
AC | AIR CONDITIONER | SUMMER | [ ] CHECK OIL LEVEL
AC | AIR CONDITIONER | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
AC | AIR CONDITIONER | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
AC | AIR CONDITIONER | SUMMER | [ ] CHECK INDOOR COIL
AC | AIR CONDITIONER | SUMMER | TEMPERATURE DROP______DEG F
AC | AIR CONDITIONER | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE________DEG F
AC | AIR CONDITIONER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
AC | AIR CONDITIONER | SUMMER | [ ] CHECK FRESH AIR INTAKE SCREENS
ACP | AIR COMPRESSOR | FALL | [ ] CHECK BELTS AND PULLEYS
ACP | AIR COMPRESSOR | FALL | [ ] CHANGE AIR FILTER
ACP | AIR COMPRESSOR | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
ACP | AIR COMPRESSOR | FALL | [ ] *CHANGE OIL
ACP | AIR COMPRESSOR | FALL | [ ] CHECK SUPPLY VOLTAGE_______________
ACP | AIR COMPRESSOR | FALL | [ ] CHECK MOTOR AMPS________________
ACP | AIR COMPRESSOR | FALL | [ ] CHECK OIL PRESSURE GUAGE
ACP | AIR COMPRESSOR | FALL | [ ] CHECK OIL LEVEL
ACP | AIR COMPRESSOR | FALL | [ ] CHECK PRV FOR PROPER SETTING
ACP | AIR COMPRESSOR | FALL | [ ] CHECK AUTO DRAIN OR MANUALLY DRAIN TANK
ACP | AIR COMPRESSOR | FALL | [ ] CHECK PRESSURE RELIEF VALVE
ACP | AIR COMPRESSOR | FALL | [ ] CHECK OPERATING CONTROL PRESSURE
ACP | AIR COMPRESSOR | FALL | [ ] AIR DRIER
ACP | AIR COMPRESSOR | FALL | [ ] CHECK OPERATING CYCLE
ACP | AIR COMPRESSOR | FALL | [ ] CHECK AUTO DRAIN
ACP | AIR COMPRESSOR | FALL
ACP | AIR COMPRESSOR | FALL | *IF COVERED
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK BELTS AND PULLEYS
ACP | AIR COMPRESSOR | WINTER | [ ] INSPECT AIR FILTER
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK CONTROL SET POINTS
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK OIL LEVEL
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK PRV FOR PROPER SETTING
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK AUTO DRAIN OR MANUALLY DRAIN TANK
ACP | AIR COMPRESSOR | WINTER | [ ] AIR DRIER
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK OPERATING CYCLE
ACP | AIR COMPRESSOR | WINTER | [ ] CHECK AUTO DRAIN
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK BELTS AND PULLEYS
ACP | AIR COMPRESSOR | SPRING | [ ] INSPECT AIR FILTER
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK CONTROL SET POINTS
ACP | AIR COMPRESSOR | SPRING | [ ] CHANGE OIL (PER MFG SPECS)
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK OIL LEVEL
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK AUTO DRAIN OR MANUALLY DRAIN TANK
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK PRV FOR PROPER SETTING
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK CAPACITY CONTROLS
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK OPERATING CONTROL PRESSURE
ACP | AIR COMPRESSOR | SPRING | [ ] MEGG / OHM MOTORS 10.0 HP OR LARGER
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK CONTACTOR POINTS
ACP | AIR COMPRESSOR | SPRING | [ ] LUBE MOTOR
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
ACP | AIR COMPRESSOR | SPRING | [ ] AIR DRIER
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK AUTO DRAIN
ACP | AIR COMPRESSOR | SPRING | [ ] CLEAN CONDENSER COIL
ACP | AIR COMPRESSOR | SPRING | [ ] CHECK OPERATING CYCLE
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK BELTS AND PULLEYS
ACP | AIR COMPRESSOR | SUMMER | [ ] INSPECT AIR FILTER
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK OIL LEVEL
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK PRV FOR PROPER SETTING
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK AUTO DRAIN OR MANUALLY DRAIN TANK
ACP | AIR COMPRESSOR | SUMMER | [ ] AIR DRIER
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK OPERATING CYCLE
ACP | AIR COMPRESSOR | SUMMER | [ ] CHECK AUTO DRAIN
ACR | AIR CURTAIN | FALL | [ ] CHECK BLET
ACR | AIR CURTAIN | FALL | [ ] CHECK PULLEY WEAR
ACR | AIR CURTAIN | FALL | [ ] CHECK DOOR INTERLOCK
ACR | AIR CURTAIN | FALL | [ ] CHECK FAN OPERATION
ACR | AIR CURTAIN | FALL | [ ] CHECK HEAT OPERATION
ACR | AIR CURTAIN | FALL | [ ] CHECK THERMOSTAT OPERATION
ACR | AIR CURTAIN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ACR | AIR CURTAIN | FALL | [ ] LUBRICATE MOTOR IF REQUIRED
ACR | AIR CURTAIN | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
ACR | AIR CURTAIN | FALL | [ ] CHECK VOLTAGE_______________________
ACR | AIR CURTAIN | WINTER | [ ] CHECK BELT
ACR | AIR CURTAIN | WINTER | [ ] CHECK PULLEY WEAR
ACR | AIR CURTAIN | WINTER | [ ] CHECK DOOR INTERLOCK
ACR | AIR CURTAIN | WINTER | [ ] CHECK FAN OPERATION
ACR | AIR CURTAIN | WINTER | [ ] CHECK HEAT OPERATION
ACR | AIR CURTAIN | WINTER | [ ] CHECK THERMOSTAT OPERATION
ACR | AIR CURTAIN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ACR | AIR CURTAIN | SPRING | [ ] CHECK BELT
ACR | AIR CURTAIN | SPRING | [ ] CHECK PULLEY WEAR
ACR | AIR CURTAIN | SPRING | [ ] CHECK DOOR INTERLOCK
ACR | AIR CURTAIN | SPRING | [ ] CHECK FAN OPERATION
ACR | AIR CURTAIN | SPRING | [ ] CHECK HEAT OPERATION
ACR | AIR CURTAIN | SPRING | [ ] CHECK THERMOSTAT OPERATION
ACR | AIR CURTAIN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ACR | AIR CURTAIN | SUMMER | [ ] CHECK BELT
ACR | AIR CURTAIN | SUMMER | [ ] CHECK PULLEY WEAR
ACR | AIR CURTAIN | SUMMER | [ ] CHECK DOOR INTERLOCK
ACR | AIR CURTAIN | SUMMER | [ ] CHECK FAN OPERATION
ACR | AIR CURTAIN | SUMMER | [ ] CHECK HEAT OPERATION
ACR | AIR CURTAIN | SUMMER | [ ] CHECK THERMOSTAT OPERATION
ACR | AIR CURTAIN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AD | AIR DRIER | FALL | [ ] CHECK AMPS______________________
AD | AIR DRIER | FALL | [ ] CHECK VOLTAGE_____________________
AD | AIR DRIER | FALL | [ ] CHECK THERMOSTAT OPERATION
AD | AIR DRIER | FALL | [ ] CHECK TEMPERATURE DROP OF AIR
AD | AIR DRIER | FALL | [ ] CHECK FAN OPERATION
AD | AIR DRIER | FALL | [ ] CHECK COMPRESSOR OPERATION
AD | AIR DRIER | FALL | [ ] INSPECT AND CLEAN CONDENSER COIL
AD | AIR DRIER | FALL | [ ] CHECK CONDENSATE AUTO DRAIN
AD | AIR DRIER | FALL | [ ] CLEAN AND REPLACE AUTO DRAIN AS NEEDED PER MFG.SPECS
AD | AIR DRIER | FALL | [ ] CHECK WATER COOLED CONDENSER (IF REQUIRED)
AD | AIR DRIER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AD | AIR DRIER | FALL | [ ] LUBRICATE FAN IF REQUIRED
AD | AIR DRIER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
AD | AIR DRIER | FALL | [ ] CHECK CONTACTOR POINTS
AD | AIR DRIER | WINTER | [ ] CHECK AMPS________________________
AD | AIR DRIER | WINTER | [ ] CHECK VOLTAGE____________________
AD | AIR DRIER | WINTER | [ ] CHECK THERMOSTAT OPERATION
AD | AIR DRIER | WINTER | [ ] CHECK TEMPERATURE DROP OF AIR
AD | AIR DRIER | WINTER | [ ] CHECK FAN OPERATION
AD | AIR DRIER | WINTER | [ ] CHECK COMPRESSOR OPERATION
AD | AIR DRIER | WINTER | [ ] INSPECT AND CLEAN CONDENSER COIL
AD | AIR DRIER | WINTER | [ ] CHECK CONDENSATE AUTO DRAIN
AD | AIR DRIER | WINTER | [ ] CLEAN AND REPLACE AUTO DRAIN AS NEEDED PER MFG. SPECS
AD | AIR DRIER | WINTER | [ ] CHECK WATER COOLED CONDENSER (IF REQUIRED)
AD | AIR DRIER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AD | AIR DRIER | WINTER | [ ] LUBRICATE FAN IF REQUIRED
AD | AIR DRIER | SPRING | [ ] CHECK AMPS_______________________
AD | AIR DRIER | SPRING | [ ] CHECK VOLTAGE___________________
AD | AIR DRIER | SPRING | [ ] CHECK THERMOSTAT OPERATION
AD | AIR DRIER | SPRING | [ ] CHECK TEMPERATURE DROP OF AIR
AD | AIR DRIER | SPRING | [ ] CHECK FAN OPERATION
AD | AIR DRIER | SPRING | [ ] CHECK COMPRESSOR OPERATION
AD | AIR DRIER | SPRING | [ ] INSPECT AND CLEAN CONDENSER COIL
AD | AIR DRIER | SPRING | [ ] CHECK CONDENSATE AUTO DRAIN
AD | AIR DRIER | SPRING | [ ] CLEAN AND REPLACE AUTO DRAIN AS NEEDED PER MFG. SPECS
AD | AIR DRIER | SPRING | [ ] CHECK WATER COOLED CONDENSER (IF REQUIRED)
AD | AIR DRIER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AD | AIR DRIER | SPRING | [ ] LUBRICATE FAN IF REQUIRED
AD | AIR DRIER | SUMMER | [ ] CHECK AMPS________________
AD | AIR DRIER | SUMMER | [ ] CHECK VOLTAGE______________
AD | AIR DRIER | SUMMER | [ ] CHECK THERMOSTAT OPERATION
AD | AIR DRIER | SUMMER | [ ] CHECK TEMPERATURE DROP OF AIR
AD | AIR DRIER | SUMMER | [ ] CHECK FAN OPERATION
AD | AIR DRIER | SUMMER | [ ] CHECK COMPRESSOR OPERATION
AD | AIR DRIER | SUMMER | [ ] INSPECT AND CLEAN CONDENSER COIL
AD | AIR DRIER | SUMMER | [ ] CHECK CONDENSATE AUTO DRAIN
AD | AIR DRIER | SUMMER | [ ] CLEAN AND REPLACE AUTO DRAIN AS NEEDED PER MFG. SPECS
AD | AIR DRIER | SUMMER | [ ] CHECK WATER COOLED CONDENSER (IF REQUIRED)
AD | AIR DRIER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AD | AIR DRIER | SUMMER | [ ] LUBRICATE FAN IF REQUIRED
AHU | AIR HANDLER | FALL | [ ] CHECK BELTS
AHU | AIR HANDLER | FALL | [ ] INSPECT CONDENSATE PAN, PUMP, AND TRAP
AHU | AIR HANDLER | FALL | [ ] ADD PAN TABS
AHU | AIR HANDLER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AHU | AIR HANDLER | FALL | [ ] CHECK CONDITION OF COIL
AHU | AIR HANDLER | FALL | [ ] CHECK PULLEY WEAR
AHU | AIR HANDLER | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
AHU | AIR HANDLER | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
AHU | AIR HANDLER | FALL | FRESH AIR CYCLE (IF EQUIPPED)
AHU | AIR HANDLER | FALL | [ ] CHECK OPERATING CONTROLS
AHU | AIR HANDLER | FALL | [ ] CHECK DAMPER OPERATION
AHU | AIR HANDLER | FALL | ELECTRIC HEAT: (IF REQUIRED)
AHU | AIR HANDLER | FALL | [ ] CHECK AMP DRAW
AHU | AIR HANDLER | FALL | [ ] CHECK CONTACTOR POINTS
AHU | AIR HANDLER | FALL | [ ] CHECK TEMPERATURE RISE
AHU | AIR HANDLER | FALL | GAS HEAT: (IF REQUIRED)
AHU | AIR HANDLER | FALL | [ ] CHECK TEMPERATURE RISE
AHU | AIR HANDLER | FALL | [ ] CHECK SEQUENCER OPERATION
AHU | AIR HANDLER | FALL | [ ] CHECK FAN SWITCH
AHU | AIR HANDLER | FALL | [ ] VISUAL CHECK OF HEAT EXCHANGER AND
AHU | AIR HANDLER | FALL | VISUAL CHECK OF FLUE
AHU | AIR HANDLER | FALL | [ ] CHECK PILOT SETTING
AHU | AIR HANDLER | FALL | [ ] CHECK MAIN LINE GAS PRESSURE
AHU | AIR HANDLER | FALL | [ ] CHECK MANIFOLD GAS PRESSURE
AHU | AIR HANDLER | FALL | [ ] CLEAN COMBUSTION BLOWER WHEEL
AHU | AIR HANDLER | FALL | [ ] OIL COMBUSTION BLOWER MOTOR
AHU | AIR HANDLER | FALL | [ ] CLEAN AND ADJUST IGNITOR
AHU | AIR HANDLER | FALL | [ ] CHECK VOLTAGE_____________________
AHU | AIR HANDLER | FALL | [ ] CHECK AMP DRAW_______________________
AHU | AIR HANDLER | WINTER | [ ] CHECK BELTS
AHU | AIR HANDLER | WINTER | [ ] INSPECT CONDENSATE PAN,PUMP, AND TRAP
AHU | AIR HANDLER | WINTER | [ ] ADD PAN TABS
AHU | AIR HANDLER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AHU | AIR HANDLER | WINTER | [ ] CHECK CONDITION OF COIL
AHU | AIR HANDLER | WINTER | [ ] CHECK VOLTAGE_________________
AHU | AIR HANDLER | WINTER | [ ] CHECK AMP DRAW____________________
AHU | AIR HANDLER | SPRING | [ ] CHECK BELTS
AHU | AIR HANDLER | SPRING | [ ] INSPECT CONDENSATE PAN, PUMP, AND TRAP
AHU | AIR HANDLER | SPRING | [ ] ADD PAN TABS
AHU | AIR HANDLER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AHU | AIR HANDLER | SPRING | [ ] CHECK CONDITION OF COIL
AHU | AIR HANDLER | SPRING | [ ] LUBRICATE BLOWER BEARINGS
AHU | AIR HANDLER | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
AHU | AIR HANDLER | SPRING | [ ] CHECK AMP DRAW____________________
AHU | AIR HANDLER | SPRING | [ ] CHECK VOLTAGE_____________________
AHU | AIR HANDLER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
AHU | AIR HANDLER | SPRING | [ ] CHECK CONTACTOR POINTS
AHU | AIR HANDLER | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
AHU | AIR HANDLER | SPRING | FRESH AIR CYCLE (IF EQUIPPED)
AHU | AIR HANDLER | SPRING | [ ] CHECK FRESH AIR SCREENS
AHU | AIR HANDLER | SPRING | [ ] LUBRICATE IF REQUIRED
AHU | AIR HANDLER | SPRING | [ ] CHECK OPERATING CONTROLS
AHU | AIR HANDLER | SPRING | [ ] CHECK DAMPER OPERATION
AHU | AIR HANDLER | SPRING | [ ] CHECK MINIMUM POSITION
AHU | AIR HANDLER | SPRING | [ ] CHECK RELIEF (IF EQUIPPED)
AHU | AIR HANDLER | SUMMER | [ ] CHECK BELTS
AHU | AIR HANDLER | SUMMER | [ ] INSPECT CONDENSATE PAN, PUMP, AND TRAP
AHU | AIR HANDLER | SUMMER | [ ] ADD PAN TABS
AHU | AIR HANDLER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
AHU | AIR HANDLER | SUMMER | [ ] CHECK CONDITION OF COIL
AHU | AIR HANDLER | SUMMER | [ ] CHECK VOLTAGE_______________________
AHU | AIR HANDLER | SUMMER | [ ] CHECK AMP DRAW__________________________
AOS | AIR/OIL SEPARATOR | FALL | [ ] INSPECT SEPARATOR OPERATION
AOS | AIR/OIL SEPARATOR | FALL | [ ] CHECK FOR OIL LEAKS
AOS | AIR/OIL SEPARATOR | WINTER | [ ] INSPECT SEPARATOR OPERATION
AOS | AIR/OIL SEPARATOR | WINTER | [ ] CHECK FOR OIL LEAKS
AOS | AIR/OIL SEPARATOR | SPRING | [ ] INSPECT SEPARATOR OPERATION
AOS | AIR/OIL SEPARATOR | SPRING | [ ] CHECK FOR OIL LEAKS
AOS | AIR/OIL SEPARATOR | SUMMER | [ ] INSPECT SEPARATOR OPERATION
AOS | AIR/OIL SEPARATOR | SUMMER | [ ] CHECK FOR OIL LEAKS
B | BOILER | FALL | [ ] VISUAL INSPECTION OF BOILER, CONTROLS, AND PIPING
B | BOILER | FALL | [ ] INSPECT BURNERS
B | BOILER | FALL | [ ] INSPECT FIRESIDE ANNUALLY
B | BOILER | FALL | [ ] OPEN AND INSPECT WATERSIDE BI-ANNUALLY
B | BOILER | FALL | [ ] INSPECT REFRACTORY
B | BOILER | FALL | [ ] DISASSEMBLE AND CLEAN LOW WATER CUT-OFFS AND
B | BOILER | FALL | FEEDWATER CONTROLS
B | BOILER | FALL | [ ] CHECK OPERATION OF ALL CONTROLS,LIMITS, SAFETIES,
B | BOILER | FALL | AND INTERLOCKS
B | BOILER | FALL | [ ] MANUALLY LIFT RELIEF VALVE AND CHECK SEATING
B | BOILER | FALL | [ ] RECORD PRESSURE/TEMPERATURE
B | BOILER | FALL | [ ] CHECK GUAGE GLASS AND FITTINGS FOR WEAR OR LEAKAGE
B | BOILER | FALL | [ ] TAKE FLUE SAMPLES: 02____________CO_________SMOKE____
B | BOILER | FALL | [ ] LUBRICATE COMBUSTION BLOWER MOTORS
B | BOILER | FALL | [ ] CHECK FEEDWATER TANKS, PUMP, AND CONTROLS
B | BOILER | FALL | [ ] CLEAN MAKE-UP PRV STRAINERS AND CHECK
B | BOILER | FALL | PRESSURE SETTING
B | BOILER | FALL | [ ] CHECK EXPANSION TANK
B | BOILER | FALL | [ ] CHECK VOLTAGE_______________________
B | BOILER | FALL | [ ] CHECK AMP DRAW_______________
B | BOILER | FALL
B | BOILER | FALL | ELECTRIC BOILERS
B | BOILER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
B | BOILER | FALL | [ ] CHECK CONTACTORS
B | BOILER | FALL | [ ] CHECK AMP DRAW ON ALL ELEMENTS
B | BOILER | FALL
B | BOILER | FALL | [ ] LOG ALL INFORMATION IN LOG BOOK
B | BOILER | FALL | [ ] OHM ALL ELEMENTS AND RECORD
B | BOILER | FALL | [ ] CHECK LOW WATER CUTOFFS AND LIMITS
B | BOILER | FALL | [ ] MANUALLY LIFT RELIEF VALVE AND CHECK SEATING
B | BOILER | WINTER | [ ] VISUAL INSPECTION OF BOILER, CONTROLS,AND PIPING
B | BOILER | WINTER | [ ] CHECK FLAME COLOR AND SIZE
B | BOILER | WINTER | [ ] CHECK MAKE-UP WATER STRAINERS
B | BOILER | WINTER | [ ] CHECK EXPANSION TANK
B | BOILER | WINTER | [ ] RECORD ENTERING AND LEAVING WATER TEMPERATURE
B | BOILER | WINTER | EWT_________________LWT______________________
B | BOILER | WINTER | [ ] CHECK AMP DRAW_____________________
B | BOILER | WINTER | [ ] CHECK VOLTAGE_________________________
B | BOILER | WINTER | [ ] CHECK OPERATING SAFETIES AND LIMITS
B | BOILER | WINTER | [ ] CHECK LOW WATER CUTOFF
B | BOILER | WINTER | [ ] MANUALLY LIFT RELIEF VALVE AND CHECK SEATING
B | BOILER | WINTER | [ ] RECORD PRESSURE/TEMPERATURE
B | BOILER | SPRING | [ ] VISUAL INSPECTION OF BOILER, CONTROLS, AND PIPING
B | BOILER | SPRING | [ ] CHECK FLAME COLOR AND SIZE
B | BOILER | SPRING | [ ] CLEAN MAKE-UP WATER STRAINERS
B | BOILER | SPRING | [ ] CHECK EXPANSION TANK
B | BOILER | SPRING | [ ] RECORD ENTERING AND LEAVING WATER TEMPERATURES
B | BOILER | SPRING | EWT_________________LWT_______________________
B | BOILER | SPRING | [ ] CHECK VOLTAGE_______________________
B | BOILER | SPRING | [ ] CHECK AMP DRAW______________________
B | BOILER | SPRING | [ ] MANUALLY LIFT RELIEF VALVE AND CHECK SEATING
B | BOILER | SPRING | [ ] RECORD PRESSURE/TEMPERATURE
B | BOILER | SPRING | [ ] CHECK LOW WATER CUTOFF
B | BOILER | SPRING | [ ] CHECK OPERATING SAFETIES AND LIMITS
B | BOILER | SUMMER | [ ] VISUAL INSPECTION OF BOILER, CONTROLS, AND PIPING
B | BOILER | SUMMER | [ ] CHECK FLAME COLOR AND SIZE
B | BOILER | SUMMER | [ ] CLEAN MAKE-UP WATER STRAINERS
B | BOILER | SUMMER | [ ] CHECK EXPANSION TANK
B | BOILER | SUMMER | [ ] RECORD ENTERING AND LEAVING WATER TEMPERATURE
B | BOILER | SUMMER | EWT_________________LWT______________________
B | BOILER | SUMMER | [ ] CHECK VOLTAGE_________________________
B | BOILER | SUMMER | [ ] CHECK AMP DRAW_________________________
B | BOILER | SUMMER | [ ] MANUALLY LIFT RELIEF VALVE AND CHECK SEATING
B | BOILER | SUMMER | [ ] RECORD PRESSURE/TEMPERATURE
B | BOILER | SUMMER | [ ] CHECK OPERATING SAFETIES AND LIMITS
B | BOILER | SUMMER | [ ] CHECK LOW WATER CUTOFF
BL | BLOWER | FALL | [ ] CHECK BELTS
BL | BLOWER | FALL | [ ] CHECK PULLEY FOR WEAR
BL | BLOWER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
BL | BLOWER | FALL | [ ] CHECK OPERATION
BL | BLOWER | FALL | [ ] CHECK AMPS_______________________
BL | BLOWER | FALL | [ ] CHECK VOLTAGE______________________
BL | BLOWER | FALL | [ ] INSPECT BLOWER FOR DIRT
BL | BLOWER | FALL | [ ] CHECK FAN CAPACITY CONTROL OPERATION
BL | BLOWER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
BL | BLOWER | FALL | [ ] CHECK CONTACTOR POINTS
BL | BLOWER | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
BL | BLOWER | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
BL | BLOWER | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
BL | BLOWER | FALL | [ ] INSPECT SPRING ISOLATION
BL | BLOWER | FALL | [ ] INSPECT FLEX CONNECTOR OR FAN SEAL
BL | BLOWER | WINTER | [ ] CHECK BELTS
BL | BLOWER | WINTER | [ ] CHECK PULLEY FOR WEAR
BL | BLOWER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
BL | BLOWER | WINTER | [ ] CHECK OPERATION
BL | BLOWER | WINTER | [ ] CHECK AMPS__________________________
BL | BLOWER | WINTER | [ ] CHECK VOLTAGE_______________________
BL | BLOWER | WINTER | [ ] INSPECT BLOWER FOR DIRT
BL | BLOWER | WINTER | [ ] CHECK FAN CAPACITY CONTROL OPERATION
BL | BLOWER | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
BL | BLOWER | SPRING | [ ] CHECK BELTS
BL | BLOWER | SPRING | [ ] CHECK PULLEY FOR WEAR
BL | BLOWER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
BL | BLOWER | SPRING | [ ] CHECK OPERATION
BL | BLOWER | SPRING | [ ] CHECK CONTACTOR POINTS
BL | BLOWER | SPRING | [ ] CHECK AMPS___________________
BL | BLOWER | SPRING | [ ] CHECK VOLTAGE___________________
BL | BLOWER | SPRING | [ ] INSPECT BLOWER FOR DIRT
BL | BLOWER | SPRING | [ ] CHECK FAN CAPACITY CONTROL OPERATION
BL | BLOWER | SUMMER | [ ] CHECK BELTS
BL | BLOWER | SUMMER | [ ] CHECK PULLEY FOR WEAR
BL | BLOWER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
BL | BLOWER | SUMMER | [ ] CHECK OPERATION
BL | BLOWER | SUMMER | [ ] CHECK AMPS___________________
BL | BLOWER | SUMMER | [ ] CHECK VOLTAGE___________________
BL | BLOWER | SUMMER | [ ] INSPECT BLOWER FOR DIRT
BL | BLOWER | SUMMER | [ ] CHECK FAN CAPACITY CONTROL OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK BELT
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK PULLEY FOR WEAR
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK CONDENSER COIL CONDITION
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK SUPPLY VOLTAGE___________________
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK FAN AMPS__________________________
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK FAN OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | FALL | [ ] CHECK HEAD PRESSURE CONTROL
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK BELT
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK PULLEY FOR WEAR
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK CONDENSER COIL CONDITION
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK SUPPLY VOLTAGE___________________-
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK FAN AMPS__________________________
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK FAN OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | WINTER | [ ] CHECK HEAD PRESSURE CONTROL
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK BELT
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK PULLEY FOR WEAR
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK CONDENSER COIL CONDITION
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK SUPPLY VOLTAGE_____________
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK FAN AMPS____________________
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK FAN OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK HEAD PRESSURE CONTROL
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK CONDENSER FAN BLADE AND SUPPORTS
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] LUBRICATE BLOWER
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK CONTACTOR POINTS
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
C | CONDENSER UNIT (W/O COMPRESSOR) | SPRING | [ ] MEG OHM MOTORS (10 HP OR LARGER)
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK BELT
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK PULLEY FOR WEAR
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK CONDENSER COIL CONDITION
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK SUPPLY VOLTAGE_______________-
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK FAN AMPS_______________________
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK OPERATION
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK FAN OPERAION
C | CONDENSER UNIT (W/O COMPRESSOR) | SUMMER | [ ] CHECK HEAD PRESSURE CONTROL
CRAC 1 & 2 | DATA AIRE COMPUTER ROOM AC'S | FALL | [ ] CHECK PULLEY WEAR
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK BELTS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK PULLEY ALIGNMENT
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CONDENSATE PAN,PUMP, AND TRAP
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] ADD PAN TABS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK INDOOR / OUTDOOR COIL CONDITION
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK SUPPLY VOLTAGE_________,_________,_________
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK MOTOR AMPS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CONTROL SET POINTS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CRANKCASE HEATER
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK OIL LEVEL
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK COMPRESSOR INDOOR COIL
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | TEMPERATURE DROP___________DEG.F.
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | #1__________#2__________#3__________
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK WATER ECONOMIZER (IF EQUIP)
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK ELECTRIC HEAT
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CALIBRATION OF TEMPERATURE CONTROLS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CALIBRATION OF ALARMS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK ALARM AND SYSTEM CONTROL SET POINTS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK ALARM LIGHT
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK CONTROL SEQUENCE - ALARMS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK HUMIDIFIER PAN AND OPERATION
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK INFRARED BULBS
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK AUTO FLUSH
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK DEHUMIDIFIER OPERATION
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK FREEZE PROTECTION_________________DEG. F.
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] CHECK NITRITE LEVEL_________________PPM
CAC | COMPUTER ROOM AIR CONDITIONER | FALL | [ ] ALTERNATE LEAD / LAG
[ ] CHANGE FILTERS
CRAC 1 & 2 | DATA AIRE COMPUTER ROOM AC'S | SPRING | [ ] CHECK BELTS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK PULLEY ALIGNMENT
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] ADD PAN TABS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK INDOOR / OUTDOOR COIL CONDITION
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK SUPPLY VOLTAGE_________,__________,__________
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK MOTOR AMPS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CONTROL SET POINTS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CRANKCASE HEATER
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK OIL LEVEL
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK COMPRESSOR INDOOR COIL
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | TEMPERATURE DROP______________DEG.F
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | #1________#2________#3________
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK WATER ECONOMIZER (IF EQUIP)
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CONTACTOR POINTS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK HOT GAS HEATING CYCLE (IF EQUIP)
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK ELECTRIC HEAT
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK INFRARED BULBS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK HUMIDIFIER OPERATION
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CK OPERATING PRESS: DISCH #1______#2______#3______
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | SUCTION #1______#2______#3______
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK SUB COOLING #1________#2________#3________
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] MEG OHM COMPRESSORS #1______#2______#3______
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | SUPPLY MOTOR #1______#2______#3______
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] LUBE MOTOR BEARINGS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK AUTO FLUSH
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK COMPRESSOR SUPER HEAT #1______#2______#3______
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK SUB COOLING
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK LEAD / LAG
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK CONTROL SEQUENCE - ALARMS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK ALARM LIGHTS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK ALARM AND SYSTEM CONTROL SET POINTS
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CHECK NITRITE LEVELS_______________PPM
CAC | COMPUTER ROOM AIR CONDITIONER | SPRING | [ ] CLEAN HUMIDIFIER PAN
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK THERMOSTAT OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK DAMPER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK BLOWER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK ELECTRIC HEAT
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] INSPECT LINKAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK TEMPERATURE RISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK AMPS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK VOLTAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK ELECTRIC CONNECTIONS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | FALL | [ ] CHECK CONTACTOR POINTS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK THERMOSTAT OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK DAMPER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK BLOWER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK ELECTRIC HEAT
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] INSPECT LINKAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK TEMPERATURE RISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK AMPS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK VOLTAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | WINTER | [ ] CHECK CONTACTOR POINTS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK THERMOSTAT OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK DAMPER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK BLOWER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK ELECTRIC HEAT
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] INSPECT LINKAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK TEMPERATURE RISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK AMPS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK VOLTAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK THERMOSTAT OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK BLOWER OPERATION
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRIC HEAT
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] INSPECT LINKAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK TEMPERATURE RISE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK AMPS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK VOLTAGE
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
CAV | CONSTANT AIR VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK CONTACTOR POINTS
CC | COOLING COIL | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CC | COOLING COIL | FALL | [ ] ADD PAN TABS
CC | COOLING COIL | FALL | [ ] INSPECT CONDENSATE PAN
CC | COOLING COIL | FALL | [ ] INSPECT CONDITION OF COIL
CC | COOLING COIL | FALL | [ ] CLEAN CONDENSATE TRAP
CC | COOLING COIL | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CC | COOLING COIL | WINTER | [ ] ADD PAN TABLETS
CC | COOLING COIL | WINTER | [ ] INSPECT CONDENSATE PAN
CC | COOLING COIL | WINTER | [ ] INSPECT CONDITION OF COIL
CC | COOLING COIL | WINTER | [ ] CLEAN CONDENSATE TRAP
CC | COOLING COIL | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CC | COOLING COIL | SPRING | [ ] ADD PAN TABLETS
CC | COOLING COIL | SPRING | [ ] INSPECT CONDENSATE PAN
CC | COOLING COIL | SPRING | [ ] INSPECT CONDITION OF COIL
CC | COOLING COIL | SPRING | [ ] CLEAN CONDENSATE TRAP
CC | COOLING COIL | SPRING | [ ] CHECK SUPERHEAT
CC | COOLING COIL | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CC | COOLING COIL | SUMMER | [ ] ADD PAN TABLETS
CC | COOLING COIL | SUMMER | [ ] INSPECT CONDENSATE PAN
CC | COOLING COIL | SUMMER | [ ] INSPECT CONDITION OF COIL
CC | COOLING COIL | SUMMER | [ ] CLEAN CONDENSATE TRAP
CCH | CENTRIFUGAL CHILLER | FALL | [ ] EVAPORATIVE PRESSURE_________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CHILLED WATER TEMP. IN_______________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CHILLED WATER TEMP. OUT______________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] REFRIGERANT TEMP. (EVAP)_____________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] COOLER LTD 3-4 = LTD DEG F________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] OIL PRESSURE_________________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] OIL SUMP TEMPERATURE_________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] OIL SUPPLY TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] BEARING TEMPERATURE__________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] OIL RETURN TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] OIL LEVEL____________________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] NET OIL PRESSURE 6-1 = N.O.P._______________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CONDENSER PRESSURE___________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CONDENSER WATER TEMPERATURE IN_______________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CONDENSER WATER TEMPERATURE OUT______________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] CONDENSER LTD 16-15 = LTD DEG F_____________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] PURGE PRESSURE_______________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] TYPE L SUCTION PRESSURE______________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] TYPE L DISCHARGE PRESSURE____________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] WATER INDICATION_____________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] PERCENT LOAD_________________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] LINE VOLTAGE_________________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] MOTOR AMPERAGE L-1___________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] L-2___________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] L-3___________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] START COUNT METER____________________________________
CCH | CENTRIFUGAL CHILLER | FALL | [ ] HOUR METER___________________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] EVAPORATIVE PRESSURE_________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CHILLED WATER TEMPERATURE IN_________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CHILLED WATER TEMPERATURE OUT________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] REFRIGERANT TEMPERATURE (EVAP)_______________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] OIL PRESSURE_________________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] COOLER LTD 3-4 = LTD DEG F___________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] OIL SUMP TEMPERATURE_________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] OIL SUPPLY TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] BEARING TEMPERATURE__________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] OIL RETURN TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] OIL LEVEL____________________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] NET OIL PRESSURE 6-1 = N.O.P._______________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CONDENSING PRESSURE__________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CONDENSER WATER TEMPERATURE IN_______________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CONDENSER WATER TEMPERATURE OUT______________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] CONDENSER LTD 16-15 = LTD DEG F______________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] PURGE PRESSURE_______________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] TYPE L SUCTION PRESSURE______________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] TYPE L DISCHARGE PRESSURE____________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] WATER INDICATION_____________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] PERCENT LOAD_________________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] LINE VOLTAGE_________________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] MOTOR AMPERAGE L-1_________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] L-2_________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] L-3_________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] START COUNT METER____________________________________
CCH | CENTRIFUGAL CHILLER | WINTER | [ ] HOUR METER___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | MAGNETIC STARTER
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHECK CONTACTS_______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHECK OVERLOADS______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHECK ARC CHUTES_____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TIGHTEN TERMINALS____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CLEAN INTERIOR_______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | MOTOR
CCH | CENTRIFUGAL CHILLER | SPRING | [ ]MEGG L-1_______L-4______MEGG BETWEEN WINDINGS_______
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TO L-2_______L-5__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] GRND L-3_______L-6__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] MOTOR COOLING VALVE__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TIGHTEN TERMINALS____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | OIL SUMP
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] MEGG MOTOR TO GROUND_________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TIGHTEN TERMINALS____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL HEATER_________TEMP_________OIL CONDITION________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL COOLER___________OIL FILTER______________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL ANALYSIS PERFORMED_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | NOTE: DE-ENERGIZE SUMP HEATER BEFORE DRAINING OIL
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] MAGNETIC STARTER_____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONTROL PANEL - CONDITIONS AND SETTINGS
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TIGHTEN ALL TERMINALS________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHECK RELAYS_________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHECK LOAD LIMIT RELAY_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] HIGH MOTOR TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LOW REFRIGERANT TEMPERATURE__________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] HIGH DISCHARGE PRESSURE______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LOW REFRIGERANT PRESSURE_____________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] HIGH OIL TEMPERATURE_________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LOW WATER TEMPERATURE________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LOW OIL TEMPERATURE__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL HEATER___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL PRESSURE_________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL COOLER___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] TIME DELAY___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL COOLER SOLENOID__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] REFRIGERANT TYPE_____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHILLED WATER FLOW SWITCH____________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CONDENSER WATER FLOW SWITCH__________________________
CCH | CENTRIFUGAL CHILLER | SPRING | PURGE UNIT
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL LEVEL____________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CLEAN PURGE DRUM_____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] RELIEF VALVE SETTING_________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CLEAN OIL SEPARATOR__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] FLOAT VALVE__________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LUBE MOTOR___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] OIL SEP. HEATER______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CHANGE COMP. OIL_____________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] REPLACE DRIER________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] ADJUST BELT__________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] WATER IN PURGE DRUM__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] HIGH PRESSURE CONTROL________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] CONDENSER CONDITION__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] EVAPORATOR CONDITION_________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] PRESSURE TEST P.S.I.G._______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] LEAK CHECK___________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] REFRIGERANT SAMPLE___________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | [ ] PERCENT OIL__________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING
CCH | CENTRIFUGAL CHILLER | SPRING | (continued next page)
CCH | CENTRIFUGAL CHILLER | SPRING | (continued)
CCH | CENTRIFUGAL CHILLER | SPRING
CCH | CENTRIFUGAL CHILLER | SPRING | OPERATIONAL CHECK
CCH | CENTRIFUGAL CHILLER | SPRING | PRELIMINARY FINAL
CCH | CENTRIFUGAL CHILLER | SPRING | VOLTS L-1_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | VOLTS L-2_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | VOLTS L-3_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | AMPS L-1_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | AMPS L-2_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | AMPS L-3_________________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | EVAPORATOR PRESSURE_______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER PRESSURE________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | OIL PRESSURE______________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | OIL SUMP TEMPERATURE______________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | OIL TEMPERATURE TO BEARINGS_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | OIL TEMPERATURE FROM BEARINGS_____________________________
CCH | CENTRIFUGAL CHILLER | SPRING | PURGE PRESSURE____________________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CHECK WATER TEMPERATURE IN________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CHECK WATER TEMPERATURE OUT_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CHECK WATER PRESSURE IN___________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CHECK WATER PRESSURE OUT__________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CHECK EVAP. TEMPERATURE___________________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER WATER TEMPERATURE IN____________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER WATER TEMPERATURE OUT___________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER WATER PRESSURE IN_______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER WATER PRESSURE OUT______________________________
CCH | CENTRIFUGAL CHILLER | SPRING | CONDENSER TEMPERATURE_____________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] EVAPORATIVE PRESSURE_________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CHILLER WATER TEMPERATURE IN_________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CHILLED WATER TEMPERATURE OUT________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] REFRIGERANT TEMPERATURE (EVAP)_______________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] COOLER LTD 3-4 = LTD DEG F_________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] OIL PRESSURE_________________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] OIL SUMP TEMPERATURE_________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] OIL SUPPLY TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] BEARING TEMPERATURE__________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] OIL RETURN TEMPERATURE_______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] OIL LEVEL____________________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] NET OIL PRESSURE 6-1 = N.O.P.______________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CONDENSING PRESSURE__________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CONDENSING WATER TEMPERATURE IN______________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CONDENSING WATER TEMPERATURE OUT_____________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] CONDENSER LTD 16-15 = LTD DEF F____________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] PURGE PRESSURE_______________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] TYPE L SUCTION PRESSURE______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] TYPE L DISCHARGE PRESSURE____________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] WATER INDICATION_____________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] PERCENT LOAD_________________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] LINE VOLTAGE_________________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] MOTOR AMPERAGE L-1_______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] L-2_______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] L-3_______________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] START COUNT METER____________________________________
CCH | CENTRIFUGAL CHILLER | SUMMER | [ ] HOUR METER___________________________________________
CF | CABINET FANS | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CF | CABINET FANS | FALL | [ ] CHECK BLOWER OPERATION
CF | CABINET FANS | FALL | [ ] CHECK BLOWER BELT
CF | CABINET FANS | FALL | [ ] CHECK PULLEY WEAR
CF | CABINET FANS | FALL | [ ] CHECK VOLTAGE____________
CF | CABINET FANS | FALL | [ ] CHECK AMP DRAW_____________
CF | CABINET FANS | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
CF | CABINET FANS | FALL | [ ] CHECK CONTACTOR POINTS
CF | CABINET FANS | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
CF | CABINET FANS | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
CF | CABINET FANS | FALL | [ ] LUBRICATE MOTOR (PER MFG SPECS)
CF | CABINET FANS | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CF | CABINET FANS | WINTER | [ ] CHECK BLOWER OPERATION
CF | CABINET FANS | WINTER | [ ] CHECK BLOWER BELT
CF | CABINET FANS | WINTER | [ ] CHECK PULLEY WEAR
CF | CABINET FANS | WINTER | [ ] CHECK VOLTAGE_______________
CF | CABINET FANS | WINTER | [ ] CHECK AMP DRAW________________
CF | CABINET FANS | SPRING | [ ] LUBRICATION BLOWER BEARING (PER MFG SPECS)
CF | CABINET FANS | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CF | CABINET FANS | SPRING | [ ] CHECK BLOWER OPERATION
CF | CABINET FANS | SPRING | [ ] CHECK BLOWER BELT
CF | CABINET FANS | SPRING | [ ] CHECK PULLEY WEAR
CF | CABINET FANS | SPRING | [ ] CHECK VOLTAGE____________________
CF | CABINET FANS | SPRING | [ ] CHECK AMP DRAW___________________
CF | CABINET FANS | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CF | CABINET FANS | SUMMER | [ ] CHECK BLOWER OPERATION
CF | CABINET FANS | SUMMER | [ ] CHECK BLOWER BELT
CF | CABINET FANS | SUMMER | [ ] CHECK PULLEY WEAR
CF | CABINET FANS | SUMMER | [ ] CHECK VOLTAGE________________
CF | CABINET FANS | SUMMER | [ ] CHECK AMP DRAW_______________
CHC | CHILLED WATER COIL | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CHC | CHILLED WATER COIL | FALL | [ ] CHECK THERMOSTATS
CHC | CHILLED WATER COIL | FALL | [ ] INSPECT CONDITION OF COIL
CHC | CHILLED WATER COIL | FALL | [ ] ADD PAN TABLETS
CHC | CHILLED WATER COIL | FALL | [ ] CLEAN CONDENSATE DRAIN TRAP
CHC | CHILLED WATER COIL | FALL | [ ] CHECK WATER VALVE OPERATION
CHC | CHILLED WATER COIL | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CHC | CHILLED WATER COIL | WINTER | [ ] CHECK THERMOSTATS
CHC | CHILLED WATER COIL | WINTER | [ ] INSPECT CONDITION OF COIL
CHC | CHILLED WATER COIL | WINTER | [ ] ADD PAN TABLETS
CHC | CHILLED WATER COIL | WINTER | [ ] CLEAN CONDENSATE DRAIN TRAP
CHC | CHILLED WATER COIL | WINTER | [ ] CHECK WATER VALVE OPERATION
CHC | CHILLED WATER COIL | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CHC | CHILLED WATER COIL | SPRING | [ ] CHECK THERMOSTATS
CHC | CHILLED WATER COIL | SPRING | [ ] INSPECT CONDITION OF COIL
CHC | CHILLED WATER COIL | SPRING | [ ] ADD PAN TABLETS
CHC | CHILLED WATER COIL | SPRING | [ ] CLEAN CONDENSATE DRAIN TRAP
CHC | CHILLED WATER COIL | SPRING | [ ] CHECK WATER VALVE OPERATION
CHC | CHILLED WATER COIL | SPRING | [ ] CHECK CHILLED WATER TEMPERATURE
CHC | CHILLED WATER COIL | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
CHC | CHILLED WATER COIL | SUMMER | [ ] CHECK THERMOSTATS
CHC | CHILLED WATER COIL | SUMMER | [ ] INSPECT CONDITION OF COIL
CHC | CHILLED WATER COIL | SUMMER | [ ] ADD PAN TABLETS
CHC | CHILLED WATER COIL | SUMMER | [ ] CLEAN CONDENSATE DRAIN TRAP
CHC | CHILLED WATER COIL | SUMMER | [ ] CHECK WATER VALVE OPERATION
CHM | CHEMICAL EQUIPMENT | FALL | !! COND.WTR !! CHILLED
CHM | CHEMICAL EQUIPMENT | FALL | !! LOOP !! WTR.LOOP
CHM | CHEMICAL EQUIPMENT | FALL | ==============================!!============!!============
CHM | CHEMICAL EQUIPMENT | FALL | !! !!
CHM | CHEMICAL EQUIPMENT | FALL | PH VALUE !! (8-10)!! (8-10)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | TOTAL DISSOLVED !! !!
CHM | CHEMICAL EQUIPMENT | FALL | SOLIDS (MICROMHOS) !! (800-1400)!! (800-1400)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | TOTAL HARDNESS !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (0-10)!! (0-10)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | CHLORIDES !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (80-120)!! (80-120)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | TOTAL ALKALINITY !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (250-350)!! (250-350)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | AVAILABLE !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ALKALINITY (PPM) !! (200-300)!! (200-300)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | ORTHO-PHOSPHATES !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (60-80)!! (60-80)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | SULFITE !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (30-60)!! (30-60)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | IRON !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (LT 0.02)!! (LT 0.02)
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | TEMPERATURE !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | FALL | FREEZE POINT !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | FALL | NITRATE !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (PPM) !! (800-1200)!! (800-1200)
CHM | CHEMICAL EQUIPMENT | FALL | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | FALL | (continued next page)
CHM | CHEMICAL EQUIPMENT | FALL | HOT.WTR !! TOWER !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | LOOP !! SUMP !! __________ !! __________ !!
CHM | CHEMICAL EQUIPMENT | FALL | ============!!============!!============!!============!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (8-10)!! (7-8.5)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (800-1400)!! (400-600)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (0-10)!! (120-180)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (80-120)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (250-350)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (200-300)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (60-80)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (30-60)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (LT 0.02)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | FALL | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | (800-1200)!! !! !! !!
CHM | CHEMICAL EQUIPMENT | FALL | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | FALL | (continued)
CHM | CHEMICAL EQUIPMENT | FALL
CHM | CHEMICAL EQUIPMENT | FALL | [ ] ADJUST TOWER BLEED IF REQUIRED
CHM | CHEMICAL EQUIPMENT | FALL | [ ] CHECK TOWER OVERFLOW
CHM | CHEMICAL EQUIPMENT | FALL | [ ] CLEAN TOWER BLEED VALVE INLET STRAINER
CHM | CHEMICAL EQUIPMENT | FALL | [ ] CHECK BLEED VALVE OPERATION IF EQUIPPED
CHM | CHEMICAL EQUIPMENT | FALL | [ ] CHECK CHEMICAL PUMP OPERATION
CHM | CHEMICAL EQUIPMENT | WINTER | !! COND.WTR !! CHILLED
CHM | CHEMICAL EQUIPMENT | WINTER | !! LOOP !! WTR.LOOP
CHM | CHEMICAL EQUIPMENT | WINTER | ==============================!!============!!============
CHM | CHEMICAL EQUIPMENT | WINTER | !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | PH VALUE !! (8-10)!! (8-10)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | TOTAL DISSOLVED !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | SOLIDS (MICROMHOS) !! (800-1400)!! (800-1400)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | TOTAL HARDNESS !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (0-10)!! (0-10)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | CHLORIDES !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (80-120)!! (80-120)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | TOTAL ALKALINITY !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (250-350)!! (250-350)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | AVAILABLE !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ALKALINITY (PPM) !! (200-300)!! (200-300)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | ORTHO-PHOSPHATES !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (60-80)!! (60-80)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | SULFITE !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (30-60)!! (30-60)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | IRON !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (LT 0.02)!! (LT 0.02)
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | TEMPERATURE !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | WINTER | FREEZE POINT !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | WINTER | NITRATE !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (PPM) !! (800-1200)!! (800-1200)
CHM | CHEMICAL EQUIPMENT | WINTER | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | WINTER | (continued next page)
CHM | CHEMICAL EQUIPMENT | WINTER | HOT.WTR !! TOWER !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | LOOP !! SUMP !! __________ !! __________ !!
CHM | CHEMICAL EQUIPMENT | WINTER | ============!!============!!============!!============!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (8-10)!! (7-8.5)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (800-1400)!! (400-600)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (0-10)!! (120-180)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (80-120)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (250-350)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (200-300)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (60-80)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (30-60)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (LT 0.02)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | WINTER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | (800-1200)!! !! !! !!
CHM | CHEMICAL EQUIPMENT | WINTER | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | WINTER | (continued)
CHM | CHEMICAL EQUIPMENT | WINTER
CHM | CHEMICAL EQUIPMENT | WINTER | [ ] ADJUST TOWER BLEED IF REQUIRED
CHM | CHEMICAL EQUIPMENT | WINTER | [ ] CHECK TOWER OVERFLOW
CHM | CHEMICAL EQUIPMENT | WINTER | [ ] CLEAN TOWER BLEED VALVE INLET STRAINER
CHM | CHEMICAL EQUIPMENT | WINTER | [ ] CHECK BLEED VALVE OPERATION IF EQUIPPED
CHM | CHEMICAL EQUIPMENT | WINTER | [ ] CHECK CHEMICAL PUMP OPERATION
CHM | CHEMICAL EQUIPMENT | SPRING | !! COND.WTR !! CHILLED
CHM | CHEMICAL EQUIPMENT | SPRING | !! LOOP !! WTR.LOOP
CHM | CHEMICAL EQUIPMENT | SPRING | ==============================!!============!!============
CHM | CHEMICAL EQUIPMENT | SPRING | !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | PH VALUE !! (8-10)!! (8-10)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | TOTAL DISSOLVED !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | SOLIDS (MICROMHOS) !! (800-1400)!! (800-1400)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | TOTAL HARDNESS !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (0-10)!! (0-10)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | CHLORIDES !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (80-120)!! (80-120)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | TOTAL ALKALINITY !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (250-350)!! (250-350)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | AVAILABLE !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ALKALINITY (PPM) !! (200-300)!! (200-300)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | ORTHO-PHOSPHATES !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (60-80)!! (60-80)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | SULFITE !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (30-60)!! (30-60)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | IRON !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (LT 0.02)!! (LT 0.02)
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | TEMPERATURE !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SPRING | FREEZE POINT !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SPRING | NITRATE !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (PPM) !! (800-1200)!! (800-1200)
CHM | CHEMICAL EQUIPMENT | SPRING | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SPRING | (continued next page)
CHM | CHEMICAL EQUIPMENT | SPRING | HOT.WTR !! TOWER !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | LOOP !! SUMP !! __________ !! __________ !!
CHM | CHEMICAL EQUIPMENT | SPRING | ============!!============!!============!!============!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (8-10)!! (7-8.5)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (800-1400)!! (400-600)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (0-10)!! (120-180)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (80-120)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (250-350)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (200-300)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (60-80)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (30-60)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (LT 0.02)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SPRING | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | (800-1200)!! !! !! !!
CHM | CHEMICAL EQUIPMENT | SPRING | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SPRING | (continued)
CHM | CHEMICAL EQUIPMENT | SPRING
CHM | CHEMICAL EQUIPMENT | SPRING | [ ] ADJUST TOWER BLEED IF REQUIRED
CHM | CHEMICAL EQUIPMENT | SPRING | [ ] CHECK TOWER OVERFLOW
CHM | CHEMICAL EQUIPMENT | SPRING | [ ] CLEAN TOWER BLEED VALVE INLET STRAINER
CHM | CHEMICAL EQUIPMENT | SPRING | [ ] CHECK BLEED VALVE OPERATION IF EQUIPPED
CHM | CHEMICAL EQUIPMENT | SPRING | [ ] CHECK CHEMICAL PUMP OPERATION
CHM | CHEMICAL EQUIPMENT | SUMMER | !! COND.WTR !! CHILLED
CHM | CHEMICAL EQUIPMENT | SUMMER | !! LOOP !! WTR.LOOP
CHM | CHEMICAL EQUIPMENT | SUMMER | ==============================!!============!!============
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | PH VALUE !! (8-10)!! (8-10)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | TOTAL DISSOLVED !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | SOLIDS (MICROMHOS) !! (800-1400)!! (800-1400)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | TOTAL HARDNESS !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (0-10)!! (0-10)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | CHLORIDES !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (80-120)!! (80-120)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | TOTAL ALKALINITY !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (250-350)!! (250-350)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | AVAILABLE !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ALKALINITY (PPM) !! (200-300)!! (200-300)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | ORTHO-PHOSPHATES !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (60-80)!! (60-80)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | SULFITE !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (30-60)!! (30-60)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | IRON !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (LT 0.02)!! (LT 0.02)
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | TEMPERATURE !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------------------------!!------------!!------------
CHM | CHEMICAL EQUIPMENT | SUMMER | FREEZE POINT !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (DEGREES F.) !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SUMMER | NITRATE !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (PPM) !! (800-1200)!! (800-1200)
CHM | CHEMICAL EQUIPMENT | SUMMER | ----------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SUMMER | (continued next page)
CHM | CHEMICAL EQUIPMENT | SUMMER | HOT.WTR !! TOWER !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | LOOP !! SUMP !! __________ !! __________ !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ============!!============!!============!!============!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (8-10)!! (7-8.5)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (800-1400)!! (400-600)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (0-10)!! (120-180)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (80-120)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (250-350)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (200-300)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (60-80)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (30-60)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (LT 0.02)!! (N/A)!! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | ------------!!------------!!------------!!------------!!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SUMMER | !! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | (800-1200)!! !! !! !!
CHM | CHEMICAL EQUIPMENT | SUMMER | --------------------------------------------------------
CHM | CHEMICAL EQUIPMENT | SUMMER | (continued)
CHM | CHEMICAL EQUIPMENT | SUMMER
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] ADJUST TOWER BLEED IF REQUIRED
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] CHECK TOWER OVERFLOW
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] CLEAN TOWER BLEED VALVE INLET STRAINER
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] CHECK BLEED VALVE OPERATION IF EQUIPPED
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] CHECK CHEMICAL PUMP OPERATION
CHM | CHEMICAL EQUIPMENT | SUMMER | [ ] OBTAIN WATER SAMPLES OF COVERED SYSTEMS. DELIVER
CHM | CHEMICAL EQUIPMENT | SUMMER | BOTTLES TO OFFICE FOR PICKUP BY CHEMICAL COMPANY.
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE____________________
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK MOTOR AMPS_________________
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK FOR SEAL LEAKS
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK PRESSURES: DISCHARGE__________SUCTION__________
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CHP | CHILLED WATER PUMP | FALL | [ ] ALTERNATE LEAD/LAG PUMP
CHP | CHILLED WATER PUMP | FALL | [ ] CHECK AUTOMATIC STAND-BY CAHNGE OVER
CHP | CHILLED WATER PUMP | FALL | [ ] LUBRICATE BEARING ASSEMBLY
CHP | CHILLED WATER PUMP | FALL | [ ] VISUALLY INSPECT COUPLING
CHP | CHILLED WATER PUMP | FALL | [ ] CLEAN AND INSPECT STRAINER
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE____________________
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK MOTOR AMPS______________________
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK PRESSURES: DISCHARGE______________
CHP | CHILLED WATER PUMP | WINTER | SUCTION______________
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK FOR SEAL LEAKS
CHP | CHILLED WATER PUMP | WINTER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CHP | CHILLED WATER PUMP | WINTER | [ ] ALTERNATE LEAD / LAG PUMP
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE_______________
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK MOTOR AMPS______________
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK PRESSURES: DISCHARGE____________
CHP | CHILLED WATER PUMP | SPRING | SUCTION____________
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK FOR SEAL LEAKS
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CHP | CHILLED WATER PUMP | SPRING | [ ] ALTERNATE LEAD / LAG PUMP
CHP | CHILLED WATER PUMP | SPRING | [ ] LUBRICATE BEARING ASSEMBLY
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK CONTACTOR/STARTER POINTS
CHP | CHILLED WATER PUMP | SPRING | [ ] CHECK CONTACTOR VOLTAGE DROP
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE________________________
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK MOTOR AMPS____________________________
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK PRESSURES: DISCHARGE_____________
CHP | CHILLED WATER PUMP | SUMMER | SUCTION_____________
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK FOR SEAL LEAKS
CHP | CHILLED WATER PUMP | SUMMER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CHP | CHILLED WATER PUMP | SUMMER | [ ] ALTERNATE LEAD / LAG PUMP
CMP | COMPRESSOR | FALL | [ ] CHECK OIL SIGHT GLASS
CMP | COMPRESSOR | FALL | [ ] CHECK UNLOADER OPERATION
CMP | COMPRESSOR | FALL | [ ] CHECK VOLTAGE______________________
CMP | COMPRESSOR | FALL | [ ] CHECK AMPS_________________________
CMP | COMPRESSOR | FALL | [ ] DISCHARGE PRESSURE_________________PSIG
CMP | COMPRESSOR | FALL | [ ] SUCTION PRESSURE___________________PSIG
CMP | COMPRESSOR | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CMP | COMPRESSOR | FALL | [ ] INSPECT FOR OIL LEAKS
CMP | COMPRESSOR | FALL | [ ] INSPECT FOR REFRIGERANT LEAKS (VISUAL)
CMP | COMPRESSOR | FALL | [ ] CHECK CRANKCASE HEATER
CMP | COMPRESSOR | FALL | [ ] CHECK OPERATION SEQUENCE
CMP | COMPRESSOR | WINTER | [ ] CHECK OIL SIGHT GLASS
CMP | COMPRESSOR | WINTER | [ ] CHECK UNLOADER OPERATION
CMP | COMPRESSOR | WINTER | [ ] CHECK VOLTAGE_______________________
CMP | COMPRESSOR | WINTER | [ ] CHECK AMPS__________________________
CMP | COMPRESSOR | WINTER | [ ] DISCHARGE PRESSURE__________________PSIG
CMP | COMPRESSOR | WINTER | [ ] SUCTION PRESSURE ___________________PSIG
CMP | COMPRESSOR | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CMP | COMPRESSOR | WINTER | [ ] INSPECT FOR OIL LEAKS
CMP | COMPRESSOR | WINTER | [ ] INSPECT FOR REFRIGERANT LEAKS (VISUAL)
CMP | COMPRESSOR | WINTER | [ ] CHECK CRANKCASE HEATER
CMP | COMPRESSOR | WINTER | [ ] CHECK OPERATIONAL SEQUENCE
CMP | COMPRESSOR | SPRING | [ ] CHECK OIL SIGHT GLASS
CMP | COMPRESSOR | SPRING | [ ] CHECK UNLOADER OPERATION
CMP | COMPRESSOR | SPRING | [ ] CHECK VOLTAGE______________________
CMP | COMPRESSOR | SPRING | [ ] CHECK AMPS_________________________
CMP | COMPRESSOR | SPRING | [ ] DISCHARGE PRESSURE_____________________PSIG
CMP | COMPRESSOR | SPRING | [ ] SUCTION PRESSURE________________________PSIG
CMP | COMPRESSOR | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CMP | COMPRESSOR | SPRING | [ ] INSPECT FOR REFRIGERANT LEAKS (VISUAL)
CMP | COMPRESSOR | SPRING | [ ] INSPECT FOR OIL LEAKS
CMP | COMPRESSOR | SPRING | [ ] CHECK CRANKCASE HEATER
CMP | COMPRESSOR | SPRING | [ ] CHECK OPERATIONAL SEQUENCE
CMP | COMPRESSOR | SPRING | [ ] CHECK SUPERHEAT AT COMPRESSOR
CMP | COMPRESSOR | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
CMP | COMPRESSOR | SPRING | [ ] TEST OIL
CMP | COMPRESSOR | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
CMP | COMPRESSOR | SPRING | [ ] CHECK CONTACTOR POINTS
CMP | COMPRESSOR | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
CMP | COMPRESSOR | SPRING | [ ] INSPECT COUPLER
CMP | COMPRESSOR | SPRING | [ ] CHECK SAFETY SWITCH SETTING AND OPERATION
CMP | COMPRESSOR | SUMMER | [ ] CHECK OIL SIGHT GLASS
CMP | COMPRESSOR | SUMMER | [ ] CHECK UNLOADER OPERATION
CMP | COMPRESSOR | SUMMER | [ ] CHECK VOLTAGE________________________
CMP | COMPRESSOR | SUMMER | [ ] CHECK AMPS___________________________
CMP | COMPRESSOR | SUMMER | [ ] DISCHARGE PRESSURE_________________PSIG
CMP | COMPRESSOR | SUMMER | [ ] SUCTION PRESSURE____________________PSIG
CMP | COMPRESSOR | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CMP | COMPRESSOR | SUMMER | [ ] INSPECT FOR OIL LEAKS
CMP | COMPRESSOR | SUMMER | [ ] INSPECT FOR REFRIGERANT LEAKS (VISUAL)
CMP | COMPRESSOR | SUMMER | [ ] CHECK CRANKCASE HEATER
CMP | COMPRESSOR | SUMMER | [ ] CHECK OPERATIONAL SEQUENCE
CNT | CONTROLS | FALL | QUARTERLY
CNT | CONTROLS | FALL
CNT | CONTROLS | FALL | SYSTEM PERFORMANCE REVIEW
CNT | CONTROLS | FALL | [ ] CHECK DAMPER ACTUATORS FOR PROPER OPERATOIN
CNT | CONTROLS | FALL | [ ] CHECK VALVE OPERATION
CNT | CONTROLS | FALL | [ ] BACK UP DATA BASE ON LOCAL PC AND SAVE ON SERVER
CNT | CONTROLS | FALL | [ ] IDENTIFY SERVICE, REPAIR OR PERFORMANCE PROBLEMS
CNT | CONTROLS | FALL | INTERVIEW BLDG CONTACT AND SERVICE TECH FOR SYSTEM
CNT | CONTROLS | FALL | EQUIPMENT, SCHEDULE AND SOFTWARE ADDS,MOVES, CHANGES
CNT | CONTROLS | FALL | AND SERVICE ISSUES
CNT | CONTROLS | FALL | [ ] UPDATE SITE INFORMATION SHEET WITH IDENTIFIED CHANGES
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY POINTS/PROGRAMS IN MANUAL, ALARM,
CNT | CONTROLS | FALL | COM FAIL, ETC.
CNT | CONTROLS | FALL | [ ] CHECK AND REVIEW ALARM LOGS
CNT | CONTROLS | FALL | [ ] CHECK AND REVIEW TREND LOGS
CNT | CONTROLS | FALL | [ ] GATHER AND REVIEW OVERRIDES
CNT | CONTROLS | FALL
CNT | CONTROLS | FALL | SEMI ANNUALLY
CNT | CONTROLS | FALL | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION REVIEW
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY LAN COMMUNICATIONS
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY MODEM CALL IN / CALL OUT
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY DAYLIGHT SAVINGS AND HOLIDAY SCHEDUL
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY EQT. RUN SCHEDULES
CNT | CONTROLS | FALL | [ ] CHECK AND VERIFY COMMON EQT. SET POINTS AND CONTROL
CNT | CONTROLS | FALL
CNT | CONTROLS | FALL | ANNUALLY
CNT | CONTROLS | FALL | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION MAINTENANCE
CNT | CONTROLS | FALL | [ ] CHECK AND CALIBRATE COMMONE EQUIPMENT PRIMARY
CNT | CONTROLS | FALL | SENSORS AND TRANSDUCERS
CNT | CONTROLS | FALL | [ ] CHECK AND REPLACE CONTROLLER BATTERY(S) WHERE APPLICA
CNT | CONTROLS | FALL | HVAC SYSTEM ADMINISTRATION
CNT | CONTROLS | FALL | [ ] REVIEW AND VERIFY FUNCTION OF EXISTING GRAPHICS SCREE
CNT | CONTROLS | FALL | [ ] REVIEW SYSTEM PROGRAMMING AND SEQUENCES OF OPERATION
CNT | CONTROLS | FALL | [ ] REVIEW OVERALL ENERGY MANAGEMENT APPLICATIONS
CNT | CONTROLS | WINTER | QUARTERLY
CNT | CONTROLS | WINTER
CNT | CONTROLS | WINTER | SYSTEM PERFORMANCE REVIEW
CNT | CONTROLS | WINTER | [ ] CHECK DAMPER ACTUATORS FOR PROPER OPERATOIN
CNT | CONTROLS | WINTER | [ ] CHECK VALVE OPERATION
CNT | CONTROLS | WINTER | [ ] BACK UP DATA BASE ON LOCAL PC AND SAVE ON SERVER
CNT | CONTROLS | WINTER | [ ] IDENTIFY SERVICE, REPAIR OR PERFORMANCE PROBLEMS
CNT | CONTROLS | WINTER | INTERVIEW BLDG CONTACT AND SERVICE TECH FOR SYSTEM
CNT | CONTROLS | WINTER | EQUIPMENT, SCHEDULE AND SOFTWARE ADDS,MOVES, CHANGES
CNT | CONTROLS | WINTER | AND SERVICE ISSUES
CNT | CONTROLS | WINTER | [ ] UPDATE SITE INFORMATION SHEET WITH IDENTIFIED CHANGES
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY POINTS/PROGRAMS IN MANUAL, ALARM,
CNT | CONTROLS | WINTER | COM FAIL, ETC.
CNT | CONTROLS | WINTER | [ ] CHECK AND REVIEW ALARM LOGS
CNT | CONTROLS | WINTER | [ ] CHECK AND REVIEW TREND LOGS
CNT | CONTROLS | WINTER | [ ] GATHER AND REVIEW OVERRIDES
CNT | CONTROLS | WINTER
CNT | CONTROLS | WINTER | SEMI ANNUALLY
CNT | CONTROLS | WINTER | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION REVIEW
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY LAN COMMUNICATIONS
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY MODEM CALL IN / CALL OUT
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY DAYLIGHT SAVINGS AND HOLIDAY SCHEDUL
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY EQT. RUN SCHEDULES
CNT | CONTROLS | WINTER | [ ] CHECK AND VERIFY COMMON EQT. SET POINTS AND CONTROL
CNT | CONTROLS | WINTER
CNT | CONTROLS | WINTER | ANNUALLY
CNT | CONTROLS | WINTER | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION MAINTENANCE
CNT | CONTROLS | WINTER | [ ] CHECK AND CALIBRATE COMMONE EQUIPMENT PRIMARY
CNT | CONTROLS | WINTER | SENSORS AND TRANSDUCERS
CNT | CONTROLS | WINTER | [ ] CHECK AND REPLACE CONTROLLER BATTERY(S) WHERE APPLICA
CNT | CONTROLS | WINTER | HVAC SYSTEM ADMINISTRATION
CNT | CONTROLS | WINTER | [ ] REVIEW AND VERIFY FUNCTION OF EXISTING GRAPHICS SCREE
CNT | CONTROLS | WINTER | [ ] REVIEW SYSTEM PROGRAMMING AND SEQUENCES OF OPERATION
CNT | CONTROLS | WINTER | [ ] REVIEW OVERALL ENERGY MANAGEMENT APPLICATIONS
CNT | CONTROLS | SPRING | QUARTERLY
CNT | CONTROLS | SPRING
CNT | CONTROLS | SPRING | SYSTEM PERFORMANCE REVIEW
CNT | CONTROLS | SPRING | [ ] CHECK DAMPER ACTUATORS FOR PROPER OPERATOIN
CNT | CONTROLS | SPRING | [ ] CHECK VALVE OPERATION
CNT | CONTROLS | SPRING | [ ] BACK UP DATA BASE ON LOCAL PC AND SAVE ON SERVER
CNT | CONTROLS | SPRING | [ ] IDENTIFY SERVICE, REPAIR OR PERFORMANCE PROBLEMS
CNT | CONTROLS | SPRING | INTERVIEW BLDG CONTACT AND SERVICE TECH FOR SYSTEM
CNT | CONTROLS | SPRING | EQUIPMENT, SCHEDULE AND SOFTWARE ADDS,MOVES, CHANGES
CNT | CONTROLS | SPRING | AND SERVICE ISSUES
CNT | CONTROLS | SPRING | [ ] UPDATE SITE INFORMATION SHEET WITH IDENTIFIED CHANGES
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY POINTS/PROGRAMS IN MANUAL, ALARM,
CNT | CONTROLS | SPRING | COM FAIL, ETC.
CNT | CONTROLS | SPRING | [ ] CHECK AND REVIEW ALARM LOGS
CNT | CONTROLS | SPRING | [ ] CHECK AND REVIEW TREND LOGS
CNT | CONTROLS | SPRING | [ ] GATHER AND REVIEW OVERRIDES
CNT | CONTROLS | SPRING
CNT | CONTROLS | SPRING | SEMI ANNUALLY
CNT | CONTROLS | SPRING | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION REVIEW
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY LAN COMMUNICATIONS
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY MODEM CALL IN / CALL OUT
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY DAYLIGHT SAVINGS AND HOLIDAY SCHEDUL
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY EQT. RUN SCHEDULES
CNT | CONTROLS | SPRING | [ ] CHECK AND VERIFY COMMON EQT. SET POINTS AND CONTROL
CNT | CONTROLS | SPRING
CNT | CONTROLS | SPRING | ANNUALLY
CNT | CONTROLS | SPRING | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION MAINTENANCE
CNT | CONTROLS | SPRING | [ ] CHECK AND CALIBRATE COMMONE EQUIPMENT PRIMARY
CNT | CONTROLS | SPRING | SENSORS AND TRANSDUCERS
CNT | CONTROLS | SPRING | [ ] CHECK AND REPLACE CONTROLLER BATTERY(S) WHERE APPLICA
CNT | CONTROLS | SPRING | HVAC SYSTEM ADMINISTRATION
CNT | CONTROLS | SPRING | [ ] REVIEW AND VERIFY FUNCTION OF EXISTING GRAPHICS SCREE
CNT | CONTROLS | SPRING | [ ] REVIEW SYSTEM PROGRAMMING AND SEQUENCES OF OPERATION
CNT | CONTROLS | SPRING | [ ] REVIEW OVERALL ENERGY MANAGEMENT APPLICATIONS
CNT | CONTROLS | SUMMER | QUARTERLY
CNT | CONTROLS | SUMMER
CNT | CONTROLS | SUMMER | SYSTEM PERFORMANCE REVIEW
CNT | CONTROLS | SUMMER | [ ] CHECK DAMPER ACTUATORS FOR PROPER OPERATOIN
CNT | CONTROLS | SUMMER | [ ] CHECK VALVE OPERATION
CNT | CONTROLS | SUMMER | [ ] BACK UP DATA BASE ON LOCAL PC AND SAVE ON SERVER
CNT | CONTROLS | SUMMER | [ ] IDENTIFY SERVICE, REPAIR OR PERFORMANCE PROBLEMS
CNT | CONTROLS | SUMMER | INTERVIEW BLDG CONTACT AND SERVICE TECH FOR SYSTEM
CNT | CONTROLS | SUMMER | EQUIPMENT, SCHEDULE AND SOFTWARE ADDS,MOVES, CHANGES
CNT | CONTROLS | SUMMER | AND SERVICE ISSUES
CNT | CONTROLS | SUMMER | [ ] UPDATE SITE INFORMATION SHEET WITH IDENTIFIED CHANGES
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY POINTS/PROGRAMS IN MANUAL, ALARM,
CNT | CONTROLS | SUMMER | COM FAIL, ETC.
CNT | CONTROLS | SUMMER | [ ] CHECK AND REVIEW ALARM LOGS
CNT | CONTROLS | SUMMER | [ ] CHECK AND REVIEW TREND LOGS
CNT | CONTROLS | SUMMER | [ ] GATHER AND REVIEW OVERRIDES
CNT | CONTROLS | SUMMER
CNT | CONTROLS | SUMMER | SEMI ANNUALLY
CNT | CONTROLS | SUMMER | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION REVIEW
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY LAN COMMUNICATIONS
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY MODEM CALL IN / CALL OUT
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY DAYLIGHT SAVINGS AND HOLIDAY SCHEDUL
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY EQT. RUN SCHEDULES
CNT | CONTROLS | SUMMER | [ ] CHECK AND VERIFY COMMON EQT. SET POINTS AND CONTROL
CNT | CONTROLS | SUMMER
CNT | CONTROLS | SUMMER | ANNUALLY
CNT | CONTROLS | SUMMER | SYSTEM CONTROL HARDWARE & SOFTWARE FUNCTION MAINTENANCE
CNT | CONTROLS | SUMMER | [ ] CHECK AND CALIBRATE COMMONE EQUIPMENT PRIMARY
CNT | CONTROLS | SUMMER | SENSORS AND TRANSDUCERS
CNT | CONTROLS | SUMMER | [ ] CHECK AND REPLACE CONTROLLER BATTERY(S) WHERE APPLICA
CNT | CONTROLS | SUMMER | HVAC SYSTEM ADMINISTRATION
CNT | CONTROLS | SUMMER | [ ] REVIEW AND VERIFY FUNCTION OF EXISTING GRAPHICS SCREE
CNT | CONTROLS | SUMMER | [ ] REVIEW SYSTEM PROGRAMMING AND SEQUENCES OF OPERATION
CNT | CONTROLS | SUMMER | [ ] REVIEW OVERALL ENERGY MANAGEMENT APPLICATIONS
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] CHECK FOR ANY TEMPERATURE SENSORS OR ANY OTHER
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | COMPONENTS THAT MIGHT BE OUT OF CALIBRATION
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] CHECK FOR ANY COMMUNICATION ERRORS OR COMPONENTS
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | THAT ARE NOT COMMUNICATING. RESET ERROR COUNTS
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | ON ALL TRUNKS
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] CHECK FOR ANY OUTPUTS THAT MIGHT BE IN A MANUAL MODE
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] CHECK AND VERIFY HVAC SYSTEM SHUTS DOWN NORMALLY
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | BASED ON THE TIME SCHEDULES AND HOLIDAY DATES
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] DOCUMENT ANY PROBLEMS FOUND DURING THE 4 CHECKS
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | NOTED ABOVE
CNTL | NEW CONTROL MAINT EQT. CODE | FALL | [ ] BACK UP THE DATABASE
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHECK FOR ANY TEMPERATURE SENDORS OR ANY OTHER
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | COMPONENTS THAT MIGHT BE OUT OF CALIBRATION
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHECK FOR ANY COMMUNICATION ERRORS OR COMPONENTS
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | THAT ARE NOT COMMUNICATING
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHECK FOR ANY OUTPUTS THAT MIGHT BE IN A MANUAL MODE
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHECK AND VERIFY HVAC SYSTEM SHUTS DOWN NORMALLY BASE
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | ON THE TIME SCHEDULES AND HOLIDAY DATES
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] DOCUMENT ANY PROBLEMS FOUND DURING THE 4 CHECKS
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | NOTED ABOVE
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] UPDATE DAYLIGHT SAVINGS AND HOLIDAY DATES FOR THE NEX
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | 12 MONTHS. CHECK WITH CUSTOMER WHICH DATES THEY WANT
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | THE HVAC SYSTEM TO BE OFF FOR HOLIDAYS AND DOCUMENT
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | THOSE DATES
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHECK WITH CUSTOMER WHAT OPERATING HOURS THEY WANT
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | THEIR HVAC SYSTEM TO RUN AND COMPARE WITH THE
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | PROGRAM AND UPDATE AS NECESSARY. DOCUMENT OPERATING
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | HOURS
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] BACK UP PROGRAM DATABASE ON LAPTOP COMPUTER AND
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | TO A FLOPPY DISK WHICH IS TO BE LEFT ON SITE.
CNTL | NEW CONTROL MAINT EQT. CODE | WINTER | [ ] CHANGE CONTROL SYSTEM BATTERY(S)
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] CHECK FOR ANY TEMPERATURE SENSORS OR ANY OTHER
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | COMPONENTS THAT MIGHT BE OUT OF CALIBRATION
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] CHECK FOR ANY COMMUNICATION ERRORS OR COMPONENTS
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | THAT ARE NOT COMMUNICATING. RESET ERROR COUNTS
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | ON ALL TRUNKS
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] CHECK FOR ANY OUTPUTS THAT MIGHT BE IN A MANUAL MODE
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] CHECK AND VERIFY HVAC SYSTEM SHUTS DOWN NORMALLY
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | BASED ON THE TIME SCHEDULES AND HOLIDAY DATES.
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] DOCUMENT ANY PROBLEMS FOUND DURING THE 4 CHECKS
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | NOTED ABOVE
CNTL | NEW CONTROL MAINT EQT. CODE | SPRING | [ ] BACK UP THE DATABASE
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] CHECK FOR ANY TEMPERATURE SENSORS OR ANY OTHER
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | COMPONENTS THAT MIGHT BE OUT OF CALIBRATION
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] CHECK FOR ANY COMMUNICATION ERRORS OR COMPONENTS
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | THAT ARE NOT COMMUNICATING. RESET ERROR COUNTS
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | ON ALL TRUNKS
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] CHECK FOR ANY OUTPUTS THAT MIGHT BE IN A MANUAL MODE
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] CHECK AND VERIFY HVAC SYSTEM SHUTS DOWN NORMALLY
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | BASED ON THE TIME SCHEDULES AND HOLIDAY DATES
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] DOCUMENT ANY PROBLEMS FOUND DURING THE 4 CHECKS
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | NOTED ABOVE
CNTL | NEW CONTROL MAINT EQT. CODE | SUMMER | [ ] BACK UP THE DATABASE
CP | CONDENSATE PUMP | FALL | [ ] CHECK SEQUENCE OF OPERATION
CP | CONDENSATE PUMP | FALL | [ ] ADD PAN TABS
CP | CONDENSATE PUMP | FALL | [ ] CHECK PAN CONDITION
CP | CONDENSATE PUMP | FALL | [ ] VERIFY CHECK VALVE OPERATION
CP | CONDENSATE PUMP | WINTER | [ ] CHECK SEQUENCE OF OPERATION
CP | CONDENSATE PUMP | WINTER | [ ] ADD PAN TABLETS
CP | CONDENSATE PUMP | WINTER | [ ] CHECK PAN CONDITION
CP | CONDENSATE PUMP | WINTER | [ ] VERIFY CHECK VALVE OPERATION
CP | CONDENSATE PUMP | SPRING | [ ] CHECK SEQUENCE OF OPERATION
CP | CONDENSATE PUMP | SPRING | [ ] ADD PAN TABLET
CP | CONDENSATE PUMP | SPRING | [ ] CHECK PAN CONDITION
CP | CONDENSATE PUMP | SPRING | [ ] VERIFY CHECK VALVE OPERATION
CP | CONDENSATE PUMP | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
CP | CONDENSATE PUMP | SUMMER | [ ] ADD PAN TABLETS
CP | CONDENSATE PUMP | SUMMER | [ ] CHECK PAN CONDITION
CP | CONDENSATE PUMP | SUMMER | [ ] VERIFY CHECK VALVE OPERATION
CT | COOLING TOWER | FALL | [ ] CHECK BELTS
CT | COOLING TOWER | FALL | [ ] CHECK BELT ALIGNMENT
CT | COOLING TOWER | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
CT | COOLING TOWER | FALL | [ ] CHECK SUPPLY VOLTAGE______________________
CT | COOLING TOWER | FALL | [ ] CHECK ECONOMIZER OPERATION
CT | COOLING TOWER | FALL | [ ] CHECK MOTOR AMPS__________________________
CT | COOLING TOWER | FALL | [ ] CHECK CONTROL SET POINTS
CT | COOLING TOWER | FALL | [ ] CLEAN SUMP
CT | COOLING TOWER | FALL | [ ] CHECK MAKE-UP WATER VALVE AND FLOAT
CT | COOLING TOWER | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
CT | COOLING TOWER | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
CT | COOLING TOWER | FALL | [ ] CHECK PULLEY WEAR
CT | COOLING TOWER | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
CT | COOLING TOWER | FALL | BINDING AND LUBE
CT | COOLING TOWER | FALL | [ ] CHECK FREEZE PROTECTION__________________DEG.F.
CT | COOLING TOWER | FALL | [ ] CHECK SUMP HEATER
CT | COOLING TOWER | FALL | [ ] CHECK HEAT TAPE
CT | COOLING TOWER | FALL | [ ] CHECK AUTO DRAIN
CT | COOLING TOWER | FALL | [ ] *CHECK CHEMICAL LEVELS:NITRITE________PPM
CT | COOLING TOWER | FALL | PH______CYCLES______
CT | COOLING TOWER | FALL | [ ] *CHECK CHEMICAL STOCK
CT | COOLING TOWER | FALL | [ ] *CHECK CHEMICAL PUMP OPERATION
CT | COOLING TOWER | FALL | [ ] *CHECK OPERATION OF AUTO DRAIN VALVE
CT | COOLING TOWER | FALL | [ ] *CHECK CHEMICAL CONTROLLER
CT | COOLING TOWER | FALL
CT | COOLING TOWER | FALL | *IF COVERED
CT | COOLING TOWER | WINTER | [ ] CHECK BELTS
CT | COOLING TOWER | WINTER | [ ] CHECK BELT ALIGNMENT
CT | COOLING TOWER | WINTER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
CT | COOLING TOWER | WINTER | [ ] CHECK SUPPLY VOLTAGE______________________
CT | COOLING TOWER | WINTER | [ ] CHECK MOTOR AMPS__________________________
CT | COOLING TOWER | WINTER | [ ] CHECK CONTROL SET POINTS
CT | COOLING TOWER | WINTER | [ ] CHECK MAKE-UP WATER VALVE AND FLOAT
CT | COOLING TOWER | WINTER | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
CT | COOLING TOWER | WINTER | [ ] CHECK PULLEY WEAR
CT | COOLING TOWER | WINTER | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
CT | COOLING TOWER | WINTER | BINDING AND LUBE
CT | COOLING TOWER | WINTER | [ ] CHECK FREEZE PROTECTION_________________DEG.F.
CT | COOLING TOWER | WINTER | [ ] CHECK SUMP HEATER
CT | COOLING TOWER | WINTER | [ ] CHECK HEAT TAPE
CT | COOLING TOWER | WINTER | [ ] CHECK AUTO DRAIN
CT | COOLING TOWER | SPRING | [ ] CHECK BELTS
CT | COOLING TOWER | SPRING | [ ] CHECK BELT ALIGNMENT
CT | COOLING TOWER | SPRING | [ ] CHECK UNUSUAL VIBRATION AND NOISE
CT | COOLING TOWER | SPRING | [ ] CHECK SUPPLY VOLTAGE________________________
CT | COOLING TOWER | SPRING | [ ] CHECK MOTOR AMPS____________________________
CT | COOLING TOWER | SPRING | [ ] CHECK CONTROL SET POINTS
CT | COOLING TOWER | SPRING | [ ] CHECK MAKE-UP WATER VALVE AND FLOAT
CT | COOLING TOWER | SPRING | [ ] CHECK SUMP WATER LEVEL
CT | COOLING TOWER | SPRING | [ ] CHECK SPRAY PUMP
CT | COOLING TOWER | SPRING | [ ] CHECK / CLEAN SPRAY PUMP STRAINER
CT | COOLING TOWER | SPRING | [ ] *CHECK CHEMICAL LEVELS NITRITE_________
CT | COOLING TOWER | SPRING | PH__________CYCLES_______
CT | COOLING TOWER | SPRING | [ ] *CHECK CHEMICAL STOCK
CT | COOLING TOWER | SPRING | [ ] *CHECK OPERATION OF AUTO DRAIN VALVE
CT | COOLING TOWER | SPRING | [ ] *CHECK CHEMICAL CONTROLLER
CT | COOLING TOWER | SPRING | [ ] *CLEAN CHEMICAL CONTROLLER SENSOR
CT | COOLING TOWER | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
CT | COOLING TOWER | SPRING | [ ] CHECK ECONOMIZER OPERATION
CT | COOLING TOWER | SPRING | [ ] CHECK COIL CONDITION FOR SCALE
CT | COOLING TOWER | SPRING | [ ] CHECK SPRAY NOZZLES
CT | COOLING TOWER | SPRING | [ ] CHECK WATER ELIMINATORS
CT | COOLING TOWER | SPRING | [ ] CLEAN SUMP
CT | COOLING TOWER | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
CT | COOLING TOWER | SPRING | [ ] CHECK CONTACTOR POINTS
CT | COOLING TOWER | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
CT | COOLING TOWER | SPRING | [ ] CHECK BL0WER WHEEL FOR DIRT
CT | COOLING TOWER | SPRING | [ ] LUBE BLOWER MOTOR
CT | COOLING TOWER | SPRING | [ ] CHECK FAN BLADES / SUPPORTS
CT | COOLING TOWER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
CT | COOLING TOWER | SPRING
CT | COOLING TOWER | SPRING | *IF COVERED
CT | COOLING TOWER | SUMMER | [ ] CHECK BELTS
CT | COOLING TOWER | SUMMER | [ ] CHECK BELT ALIGNMENT
CT | COOLING TOWER | SUMMER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
CT | COOLING TOWER | SUMMER | [ ] CHECK SUPPLY VOLTAGE___________________________
CT | COOLING TOWER | SUMMER | [ ] CHECK MOTOR AMPS_______________________________
CT | COOLING TOWER | SUMMER | [ ] CHECK CONTROL SET POINTS
CT | COOLING TOWER | SUMMER | [ ] CHECK MAKE-UP WATER VALVE AND FLOAT
CT | COOLING TOWER | SUMMER | [ ] CHECK SUMP WATER LEVEL
CT | COOLING TOWER | SUMMER | [ ] CHECK SPRAY PUMP
CT | COOLING TOWER | SUMMER | [ ] CHECK/CLEAN SPRAY PUMP STRAINER
CT | COOLING TOWER | SUMMER | [ ] *CHECK CHEMICAL LEVELS NITRITE________
CT | COOLING TOWER | SUMMER | PH__________CYCLES_______
CT | COOLING TOWER | SUMMER | [ ] *CHECK CHEMICAL STOCK
CT | COOLING TOWER | SUMMER | [ ] *CHECK OPERATION OF CHEMICAL PUMP
CT | COOLING TOWER | SUMMER | [ ] *CHECK OPERATION OF AUTO DRAIN VALVE
CT | COOLING TOWER | SUMMER | [ ] *CHECK CHEMICAL CONTROLLER
CT | COOLING TOWER | SUMMER | [ ] *CLEAN CHEMICAL CONTROLLER SENSOR
CT | COOLING TOWER | SUMMER | [ ] CHECK BLOWER WHEEL FOR DIRT
CT | COOLING TOWER | SUMMER | [ ] CHECK ECONOMIZER OPERATION
CT | COOLING TOWER | SUMMER
CT | COOLING TOWER | SUMMER | *IF COVERED
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK BELTS
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK PULLEY WEAR
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK COIL CONDITION
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK SUPPLY VOLTAGE_________________________
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK MOTOR AMPS_____________________________
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK CRANKCASE HEATER
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK OIL LEVEL
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK COOLING SEQUENCE OF OPERATION
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK DISCHARGE TEMPERATURE__________________DEG.F.
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] INSPECT FAN BLADES AND SUPPORTS
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK SAFETY OPERATION AND SETTING
CU | CONDENSER UNIT (W/COMPRESSOR) | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK BELTS
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK PULLEY WEAR
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK COIL CONDITION
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK CRANKCASE HEATER
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK DISCHARGE TEMPERATURE___________________DEG F.
CU | CONDENSER UNIT (W/COMPRESSOR) | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK BELTS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK PULLEY WEAR
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK COIL CONDITION
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK SUPPLY VOLTAGE_________________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK MOTOR AMPS_____________________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK CRANKCASE HEATER
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK OIL LEVEL
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK COOLING SEQUENCE OF OPERATION
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK DISCHARGE TEMPERATURE______________DEG F.
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK SUB COOLING_________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE_______________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK CAPACITY CONTROL
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK SAFETIES
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK DISCHARGE PRESSURE____________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK SUCTION PRESSURE__________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK CONTROL POINTS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] INSPECT FAN BLADES AND SUPPORTS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK SAFETY OPERATION AND SETTING
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] INSPECT CONTACTOR POINTS
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
CU | CONDENSER UNIT (W/COMPRESSOR) | SPRING | [ ] OIL TEST SEMI-HERMETICS
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK BELTS
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK PULLEY WEAR
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK COIL CONDITION
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK SUPPLY VOLTAGE_____________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK MOTOR AMPS_________________________
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK CRANKCASE HEATER
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK OIL LEVEL
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK COOLING SEQUENCE OF OPERATION
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK DISCHARGE TEMPERATURE___________DEG F
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK FOR REFRIGERANT LEAK (VISUAL)
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE______________
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK CAPACITY CONTROL
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK SAFETIES
CU | CONDENSER UNIT (W/COMPRESSOR) | SUMMER | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
CUH | CABINET UNIT HEATER | FALL | [ ] CHECK THERMOSTAT OPERATION
CUH | CABINET UNIT HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
CUH | CABINET UNIT HEATER | FALL | [ ] CHECK FAN OPERATION
CUH | CABINET UNIT HEATER | FALL | [ ] LUBRICATE FAN
CUH | CABINET UNIT HEATER | FALL | [ ] CHECK HEATER OPERATION
CUH | CABINET UNIT HEATER | FALL | [ ] CHECK TEMPERATURE RISE_____________________DEG.F.
CUH | CABINET UNIT HEATER | WINTER | [ ] CHECK THERMOSTAT OPERATION
CUH | CABINET UNIT HEATER | WINTER | [ ] CHECK FAN OPERATION
CUH | CABINET UNIT HEATER | WINTER | [ ] CHECK HEATER OPERATION
CUH | CABINET UNIT HEATER | WINTER | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
CUH | CABINET UNIT HEATER | SPRING | [ ] CHECK THERMOSTAT OPERATION
CUH | CABINET UNIT HEATER | SPRING | [ ] CHECK FAN OPERATION
CUH | CABINET UNIT HEATER | SPRING | [ ] CHECK HEATER OPERATION
CUH | CABINET UNIT HEATER | SPRING | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
CUH | CABINET UNIT HEATER | SUMMER | [ ] CHECK THERMOSTAT OPERATION
CUH | CABINET UNIT HEATER | SUMMER | [ ] CHECK FAN OPERATION
CUH | CABINET UNIT HEATER | SUMMER | [ ] CHECK HEATER OPERATION
CUH | CABINET UNIT HEATER | SUMMER | [ ] CHECK TEMPERATURE RISE___________________DEG.F.
CV | CONVERTER | FALL | [ ] CHECK TEMPERATURE CONTROL
CV | CONVERTER | FALL | [ ] CHECK STEAM VALVE OPERATION
CV | CONVERTER | FALL | [ ] CHECK CONDENSATE TRAP
CV | CONVERTER | FALL | [ ] CHECK HOT WATER IN AND OUT TEMPERATURE
CV | CONVERTER | WINTER | [ ] CHECK TEMPERATURE CONTROL
CV | CONVERTER | WINTER | [ ] CHECK STEAM VALVE OPERATION
CV | CONVERTER | WINTER | [ ] CHECK CONDENSATE TRAP
CV | CONVERTER | WINTER | [ ] CHECK HOT WATER IN AND OUT TEMPERATURE
CV | CONVERTER | SPRING | [ ] CHECK TEMPERATURE CONTROL
CV | CONVERTER | SPRING | [ ] CHECK STEAM VALVE OPERATION
CV | CONVERTER | SPRING | [ ] CHECK CONDENSATE TRAP
CV | CONVERTER | SPRING | [ ] CHECK HOT WATER IN AND OUT TEMPERATURE
CV | CONVERTER | SUMMER | [ ] CHECK TEMPERATURE CONTROL
CV | CONVERTER | SUMMER | [ ] CHECK STEAM VALVE OPERATION
CV | CONVERTER | SUMMER | [ ] CHECK CONDENSATE TRAP
CV | CONVERTER | SUMMER | [ ] CHECK HOT WATER IN AND OUT TEMPERATURE
CVL | CONTROL VALVE | FALL | [ ] VERIFY VALVE OPERATION
CVL | CONTROL VALVE | FALL | [ ] CHECK FOR WATER LEAKS
CVL | CONTROL VALVE | WINTER | [ ] VERIFY VALVE OPERATION
CVL | CONTROL VALVE | WINTER | [ ] CHECK FOR WATER LEAKS
CVL | CONTROL VALVE | SPRING | [ ] VERIFY VALVE OPERATIONS
CVL | CONTROL VALVE | SPRING | [ ] CHECK FOR WATER LEAKS
CVL | CONTROL VALVE | SUMMER | [ ] VERIFY VALVE OPERATION
CVL | CONTROL VALVE | SUMMER | [ ] CHECK FOR WATER LEAKS
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE______________________
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK MOTOR AMPS__________________________
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK PRESSURES: DISCHARGE_____________
CWP | CONDENSER WATER PUMP | FALL | SUCTION_____________
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK FOR SEAL LEAKS
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CWP | CONDENSER WATER PUMP | FALL | [ ] ALTERNATE LEAD / LAG PUMP
CWP | CONDENSER WATER PUMP | FALL | [ ] CHECK AUTOMATIC STAND-BY CHANGE OVER
CWP | CONDENSER WATER PUMP | FALL | [ ] LUBRICATE BEARING ASSEMBLY
CWP | CONDENSER WATER PUMP | FALL | [ ] LUBRICATE PUMP MOTOR BEARINGS
CWP | CONDENSER WATER PUMP | FALL | [ ] VISUALLY INSPECT COUPLING
CWP | CONDENSER WATER PUMP | FALL | [ ] CLEAN AND INSPECT STRAINER
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE_____________________
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK MOTOR AMPS_________________________
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK PRESSURES: DISCHARGE_______________
CWP | CONDENSER WATER PUMP | WINTER | SUCTION_______________
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK FOR SEAL LEAKS
CWP | CONDENSER WATER PUMP | WINTER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CWP | CONDENSER WATER PUMP | WINTER | [ ] ALTERNATE LEAD / LAG PUMP
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE______________________
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK CONTACTOR POINTS
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK MOTOR AMPS__________________________
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK PRESSURES: DISCHARGE_____________
CWP | CONDENSER WATER PUMP | SPRING | SUCTION_____________
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK FOR SEAL LEAKS
CWP | CONDENSER WATER PUMP | SPRING | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CWP | CONDENSER WATER PUMP | SPRING | [ ] ALTERNATE LEAD / LAG PUMP
CWP | CONDENSER WATER PUMP | SPRING | [ ] LUBRICATE BEARING ASSEMBLY
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE__________________________
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK MOTOR AMPS______________________________
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK PRESSURES: DISCHARGE_____________
CWP | CONDENSER WATER PUMP | SUMMER | SUCTION_____________
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK FOR SEAL LEAKS
CWP | CONDENSER WATER PUMP | SUMMER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
CWP | CONDENSER WATER PUMP | SUMMER | [ ] ALTERNATE LEAD / LAG PUMP
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] PUMP PRESSURE __________________
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK OPERATIONAL CYCLE
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK PUMP PRESSURE CONTROLS
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK PUMP TRANSITION
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] ALTERNATE LEAD/LAG
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] INSPECT FOR WATER LEAKS
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK WATER FILTER
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK AMPS________________
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK VOLTAGE_____________
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK AUTOMATIC CHANGE OVER
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK CONTACTOR POINTS
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK ELETRICAL CONNECTIONS
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] CHECK SAFETIES
DBP | DOMESTIC WATER BOOSTER PUMP | FALL | [ ] LUBRICATE MOTORS (PER MFG SPECS)
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] PUMP PRESSURE______________________
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK OPERATIONAL CYCLE
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK PUMP PRESSURE CONTROLS
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK PUMP TRANSITION
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] ALTERNATE LEAD/LAG
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] INSPECT FOR WATER LEAKS
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK WATER FILTER
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK AMPS_________________
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK VOLTAGE________________
DBP | DOMESTIC WATER BOOSTER PUMP | WINTER | [ ] CHECK AUTOMATIC CHANGE OVER
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] PUMP PRESSURE__________________
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK OPERATIONAL CYCLE
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK PUMP PRESSURE CONTROLS
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK PUMP TRANSITION
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] ALTERNATE LEAD/LAG
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] INSPECT FOR WATER LEAKS
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK WATER FILTER
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK AMPS_________________
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK VOLTAGE________________
DBP | DOMESTIC WATER BOOSTER PUMP | SPRING | [ ] CHECK AUTOMATIC CHANGE-OVER
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] PUMP PRESSURE____________________
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK OPERATIONAL CYCLE
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK PUMP PRESSURE CONTROLS
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK PUMP TRANSITION
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] ALTERNATE LEAD/LAG
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] INSPECT FOR WATER LEAKS
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK WATER FILTER
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK AMPS_________________
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK VOLTAGE________________
DBP | DOMESTIC WATER BOOSTER PUMP | SUMMER | [ ] CHECK AUTOMATIC CHANGE-OVER
DC | DRY COOLER | FALL | [ ] CHECK FAN AMPS______________________
DC | DRY COOLER | FALL | [ ] CHECK VOLTAGE_______________________
DC | DRY COOLER | FALL | [ ] CHECK TEMPERATURE CONTROL OPERATION
DC | DRY COOLER | FALL | [ ] CHECK FAN OPERATION
DC | DRY COOLER | FALL | [ ] INSPECT CONDITION OF COIL
DC | DRY COOLER | FALL | [ ] INSPECT EXPANSION TANK
DC | DRY COOLER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DC | DRY COOLER | FALL | [ ] CHECK FAN BLADES FOR CRACK
DC | DRY COOLER | FALL | [ ] CHECK GLYCOL CONCENTRATION
DC | DRY COOLER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
DC | DRY COOLER | FALL | [ ] CHECK CONTACTOR POINTS
DC | DRY COOLER | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
DC | DRY COOLER | FALL | [ ] CHECK FREEZE PROTECTIONS___________________DEG.F.
DC | DRY COOLER | WINTER | [ ] CHECK FAN AMPS__________________
DC | DRY COOLER | WINTER | [ ] CHECK VOLTAGE____________________
DC | DRY COOLER | WINTER | [ ] CHECK TEMPERATURE CONTROL OPERATIONS
DC | DRY COOLER | WINTER | [ ] CHECK FAN OPERATION
DC | DRY COOLER | WINTER | [ ] INSPECT CONDITION OF COIL
DC | DRY COOLER | WINTER | [ ] INSPECT EXPANSION TANK
DC | DRY COOLER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DC | DRY COOLER | WINTER | [ ] CHECK FAN BLADES FOR CRACKS
DC | DRY COOLER | SPRING | [ ] CHECK FAN AMPS_____________________
DC | DRY COOLER | SPRING | [ ] CHECK VOLTAGE_______________________
DC | DRY COOLER | SPRING | [ ] CHECK TEMPERATURE CONTROL OPERATION
DC | DRY COOLER | SPRING | [ ] CHECK FAN OPERATION
DC | DRY COOLER | SPRING | [ ] INSPECT CONDITION OF COIL
DC | DRY COOLER | SPRING | [ ] INSPECT EXPANSION TANK
DC | DRY COOLER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DC | DRY COOLER | SPRING | [ ] CHECK FAN BLADES FOR CRACKS
DC | DRY COOLER | SUMMER | [ ] CHECK FAN AMPS____________________
DC | DRY COOLER | SUMMER | [ ] CHECK VOLTAGE______________________
DC | DRY COOLER | SUMMER | [ ] CHECK TEMPERATURE CONTROL OPERATION
DC | DRY COOLER | SUMMER | [ ] CHECK CAN OPERATION
DC | DRY COOLER | SUMMER | [ ] INSPECT CONDITION OF COIL
DC | DRY COOLER | SUMMER | [ ] INSPECT EXPANSION TANK
DC | DRY COOLER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DC | DRY COOLER | SUMMER | [ ] CHECK FAN BLADES FOR CRACKS
DH | DUCT HEATER | FALL | [ ] CHECK AIR FLOW SWITCH
DH | DUCT HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
DH | DUCT HEATER | FALL | [ ] CHECK AMP DRAW ____________________AMPS
DH | DUCT HEATER | FALL | [ ] CHECK TEMPERATURE RISE_________________DEG. F.
DH | DUCT HEATER | FALL | [ ] CHECK ALL OTHER CONTROLS
DH | DUCT HEATER | WINTER | [ ] CHECK AIR FLOW SWITCH
DH | DUCT HEATER | WINTER | [ ] CHECK AMP DRAW_____________________AMPS
DH | DUCT HEATER | WINTER | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
DH | DUCT HEATER | WINTER | [ ] CHECK ALL OTHER CONTROLS
DH | DUCT HEATER | WINTER | [ ] CHECK CONTACTOR POINTS
DH | DUCT HEATER | WINTER | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
DH | DUCT HEATER | SPRING | [ ] CHECK AIR FLOW SWITCH
DH | DUCT HEATER | SPRING | [ ] CHECK AMP DRAW___________________AMPS
DH | DUCT HEATER | SPRING | [ ] CHECK TEMPERATURE RISE_______________DEG.F.
DH | DUCT HEATER | SPRING | [ ] CHECK ALL OTHER CONTROLS
DH | DUCT HEATER | SUMMER | [ ] CHECK AIR FLOW SWITCHES
DH | DUCT HEATER | SUMMER | [ ] CHECK AMP DRAW_____________________AMPS
DH | DUCT HEATER | SUMMER | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
DH | DUCT HEATER | SUMMER | [ ] CHECK ALL OTHER CONTROLS
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK FOR WATER LEAKS
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK OPERATIONAL CYCLE
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK CONDENSATE DRAIN
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK HUMIDITY CONTROL
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK VOLTAGE____________________
DHUM | DEHUMIDIFIER | FALL | [ ] CHECK AMP DRAW__________________
DHUM | DEHUMIDIFIER | FALL | [ ] OIL LEVEL_______________________
DHUM | DEHUMIDIFIER | FALL | [ ] CONDENSER WATER TEMPERATURE IN___________
DHUM | DEHUMIDIFIER | FALL | [ ] CONDENSER WATER TEMPERATURE OUT___________
DHUM | DEHUMIDIFIER | FALL | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)__________
DHUM | DEHUMIDIFIER | FALL | [ ] LINE VOLTAGE_______________________
DHUM | DEHUMIDIFIER | FALL | [ ] MOTOR AMPERAGE L-1______________
DHUM | DEHUMIDIFIER | FALL | L-2______________
DHUM | DEHUMIDIFIER | FALL | L-3______________
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK FOR WATER LEAKS
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK OPERATIONAL CYCLE
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK CONDENSATE DARAIN
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK HUMIDITY CONTROL
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK VOLTAGE_______________
DHUM | DEHUMIDIFIER | WINTER | [ ] CHECK AMP DRAW_______________
DHUM | DEHUMIDIFIER | WINTER | [ ] OIL LEVEL________________________
DHUM | DEHUMIDIFIER | WINTER | [ ] CONDENSER WATER TEMPERATURE IN____________
DHUM | DEHUMIDIFIER | WINTER | [ ] CONDENSER WATER TEMPERATURE OUT____________
DHUM | DEHUMIDIFIER | WINTER | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)_______
DHUM | DEHUMIDIFIER | WINTER | [ ] LINE VOLTAGE_____________________
DHUM | DEHUMIDIFIER | WINTER | [ ] MOTOR AMPERAGE L-1__________
DHUM | DEHUMIDIFIER | WINTER | L-2__________
DHUM | DEHUMIDIFIER | WINTER | L-3__________
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK FOR WATER LEAKS
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK OPERATIONAL CYCLE
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK CONDENSATE DRAIN
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK HUMIDITY CONTROL
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK VOLTAGE_________________
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK AMP DRAW_______________
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK CONDENSER COIL AND FAN
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK REFRIGERATION CYCLE
DHUM | DEHUMIDIFIER | SPRING | [ ] OIL LEVEL__________________
DHUM | DEHUMIDIFIER | SPRING | [ ] NET OIL PRESSURE 6-1 = N.O.P.__________________
DHUM | DEHUMIDIFIER | SPRING | [ ] CONDENSER WATER TEMPERATURE IN_______________
DHUM | DEHUMIDIFIER | SPRING | [ ] CONDENSER WATER TEMPERATURE OUT________________
DHUM | DEHUMIDIFIER | SPRING | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)____________
DHUM | DEHUMIDIFIER | SPRING | [ ] TYPE L SUCTION PRESSURE_____________________
DHUM | DEHUMIDIFIER | SPRING | [ ] TYPE L DISCHARGE PRESSURE____________________
DHUM | DEHUMIDIFIER | SPRING | [ ] LINE VOLTAGE__________________
DHUM | DEHUMIDIFIER | SPRING | [ ] MOTOR AMPERAGE L-1__________
DHUM | DEHUMIDIFIER | SPRING | L-2__________
DHUM | DEHUMIDIFIER | SPRING | L-3__________
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK CONTACTOR POINTS
DHUM | DEHUMIDIFIER | SPRING | [ ] CHECK CALIBRATION OF HUMIDITY CONTROL
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK FOR WATER LEAKS
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK OPERATIONAL CYCLE
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK CONDENSATE DRAIN
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK HUMIDITY CONTROL
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK VOLTAGE_______________
DHUM | DEHUMIDIFIER | SUMMER | [ ] CHECK AMP DRAW_______________
DHUM | DEHUMIDIFIER | SUMMER | [ ] OIL LEVEL___________________
DHUM | DEHUMIDIFIER | SUMMER | [ ] CONDENSER WATER TEMPERATURE IN__________
DHUM | DEHUMIDIFIER | SUMMER | [ ] CONDENSER WATER TEMPERATURE OUT__________
DHUM | DEHUMIDIFIER | SUMMER | [ ] LIQUID REFRIGERANT TEMPERATURE (COND)_________
DHUM | DEHUMIDIFIER | SUMMER | [ ] LINE VOLTAGE________________
DHUM | DEHUMIDIFIER | SUMMER | [ ] MOTOR AMPERAGE L-1__________
DHUM | DEHUMIDIFIER | SUMMER | L-2__________
DHUM | DEHUMIDIFIER | SUMMER | L-3__________
DMP | DAMPER | FALL | [ ] CHECK DAMPER LINKAGE
DMP | DAMPER | FALL | [ ] CHECK DAMPER ACTUATOR OPERATION
DMP | DAMPER | FALL | [ ] CHECK TEMPERATURE CONTROL
DMP | DAMPER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DMP | DAMPER | WINTER | [ ] CHECK DAMPER LINKAGE
DMP | DAMPER | WINTER | [ ] CHECK DAMPER ACTUATOR OPERATION
DMP | DAMPER | WINTER | [ ] CHECK TEMPERATURE CONTROL
DMP | DAMPER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DMP | DAMPER | SPRING | [ ] CHECK DAMPER LINKAGE
DMP | DAMPER | SPRING | [ ] CHECK DAMPER ACTUATOR OPERATION
DMP | DAMPER | SPRING | [ ] CHECK TEMPERATURE CONTROL
DMP | DAMPER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DMP | DAMPER | SUMMER | [ ] CHECK DAMPER LINKAGE
DMP | DAMPER | SUMMER | [ ] CHECK DAMPER ACTUATOR OPERATION
DMP | DAMPER | SUMMER | [ ] CHECK TEMPERATURE CONTROL
DMP | DAMPER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
DMU | DOUBLE DUCT MIXING UNIT | FALL | [ ] CHECK THERMOSTATS OPERATION
DMU | DOUBLE DUCT MIXING UNIT | FALL | [ ] CHECK DAMPER ACTUATOR OPERATION
DMU | DOUBLE DUCT MIXING UNIT | FALL | [ ] CHECK LINKAGE
DMU | DOUBLE DUCT MIXING UNIT | WINTER | [ ] CHECK THERMOSTAT OPERATION
DMU | DOUBLE DUCT MIXING UNIT | WINTER | [ ] CHECK DAMPER ACTUATOR OPERATION
DMU | DOUBLE DUCT MIXING UNIT | WINTER | [ ] CHECK LINKAGE
DMU | DOUBLE DUCT MIXING UNIT | SPRING | [ ] CHECK THERMOSTAT OPERATION
DMU | DOUBLE DUCT MIXING UNIT | SPRING | [ ] CHECK DAMPER ACTUATOR OPERATION
DMU | DOUBLE DUCT MIXING UNIT | SPRING | [ ] CHECK LINKAGE
DMU | DOUBLE DUCT MIXING UNIT | SUMMER | [ ] CHECK THERMOSTAT OPERATION
DMU | DOUBLE DUCT MIXING UNIT | SUMMER | [ ] CHECK DAMPER ACTUATOR OPERATION
DMU | DOUBLE DUCT MIXING UNIT | SUMMER | [ ] CHECK LINKAGE
DXC | DIRECT EXPANSION COIL | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
DXC | DIRECT EXPANSION COIL | FALL | [ ] ADD PAN TABLETS
DXC | DIRECT EXPANSION COIL | FALL | [ ] INSPECT CONDENSATE PAN
DXC | DIRECT EXPANSION COIL | FALL | [ ] INSPECT CONDITION OF COIL
DXC | DIRECT EXPANSION COIL | FALL | [ ] CLEAN CONDENSATE TRAP
DXC | DIRECT EXPANSION COIL | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
DXC | DIRECT EXPANSION COIL | WINTER | [ ] ADD PAN TABLETS
DXC | DIRECT EXPANSION COIL | WINTER | [ ] INSPECT CONDENSATE PAN
DXC | DIRECT EXPANSION COIL | WINTER | [ ] INSPECT CONDITION OF COIL
DXC | DIRECT EXPANSION COIL | WINTER | [ ] CLEAN CONDENSATE TRAP
DXC | DIRECT EXPANSION COIL | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
DXC | DIRECT EXPANSION COIL | SPRING | [ ] ADD PAN TABLETS
DXC | DIRECT EXPANSION COIL | SPRING | [ ] INSPECT CONDENSATE PAN
DXC | DIRECT EXPANSION COIL | SPRING | [ ] INSPECT CONDITION OF COIL
DXC | DIRECT EXPANSION COIL | SPRING | [ ] CLEAN CONDENSATE TRAP
DXC | DIRECT EXPANSION COIL | SPRING | [ ] CHECK SUPERHEAT
DXC | DIRECT EXPANSION COIL | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
DXC | DIRECT EXPANSION COIL | SUMMER | [ ] ADD PAN TABLETS
DXC | DIRECT EXPANSION COIL | SUMMER | [ ] INSPECT CONDENSATE PAN
DXC | DIRECT EXPANSION COIL | SUMMER | [ ] INSPECT CONDITION ON COIL
DXC | DIRECT EXPANSION COIL | SUMMER | [ ] CLEAN CONDENSATE TRAP
EAC | ELECTRONIC AIR CLEANER | FALL | [ ] INSPECT COLLECTOR PLATES
EAC | ELECTRONIC AIR CLEANER | FALL | [ ] INSPECT IONIZING WIRES
EAC | ELECTRONIC AIR CLEANER | FALL | [ ] CHECK TRANSFORMER OUTPUT
EAC | ELECTRONIC AIR CLEANER | FALL | [ ] CHECK FLOW SWITCH OPERATION
EAC | ELECTRONIC AIR CLEANER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EAC | ELECTRONIC AIR CLEANER | WINTER | [ ] INSPECT COLLECTOR PLATES
EAC | ELECTRONIC AIR CLEANER | WINTER | [ ] INSPECT IONIZING WIRES
EAC | ELECTRONIC AIR CLEANER | WINTER | [ ] CHECK TRANSFORMER OUTPUT
EAC | ELECTRONIC AIR CLEANER | WINTER | [ ] CHECK FLOW SWITCH OPERATION
EAC | ELECTRONIC AIR CLEANER | SPRING | [ ] INSPECT COLLECTOR PLATES
EAC | ELECTRONIC AIR CLEANER | SPRING | [ ] INSPECT IONIZING WIRES
EAC | ELECTRONIC AIR CLEANER | SPRING | [ ] CHECK TRANSFORMER OUTPUT
EAC | ELECTRONIC AIR CLEANER | SPRING | [ ] CHECK FLOW SWITCH OPERATION
EAC | ELECTRONIC AIR CLEANER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
EAC | ELECTRONIC AIR CLEANER | SUMMER | [ ] INSPECT COLLECTOR PLATES
EAC | ELECTRONIC AIR CLEANER | SUMMER | [ ] INSPECT IONIZING WIRES
EAC | ELECTRONIC AIR CLEANER | SUMMER | [ ] CHECK TRANSFORMER OUTPUT
EAC | ELECTRONIC AIR CLEANER | SUMMER | [ ] CHECK FLOW SWITCH OPERATION
EBB | ELECTRIC BASEBOARD HEATER | FALL | [ ] CHECK THERMOSTAT OPERATION
EBB | ELECTRIC BASEBOARD HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EBB | ELECTRIC BASEBOARD HEATER | FALL | [ ] CHECK AMP DRAW
EBB | ELECTRIC BASEBOARD HEATER | FALL | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
EBB | ELECTRIC BASEBOARD HEATER | WINTER | [ ] CHECK THERMOSTAT OPERATION
EBB | ELECTRIC BASEBOARD HEATER | WINTER | [ ] CHECK AMP DRAW___________________AMPS
EBB | ELECTRIC BASEBOARD HEATER | WINTER | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
EBB | ELECTRIC BASEBOARD HEATER | SPRING | [ ] CHECK THERMOSTAT OPERATION
EBB | ELECTRIC BASEBOARD HEATER | SPRING | [ ] CHECK AMP DRAW_____________________AMPS
EBB | ELECTRIC BASEBOARD HEATER | SPRING | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
EBB | ELECTRIC BASEBOARD HEATER | SUMMER | [ ] CHECK THERMOSTAT OPERATION
EBB | ELECTRIC BASEBOARD HEATER | SUMMER | [ ] CHECK AMP DRAW____________________AMPS
EBB | ELECTRIC BASEBOARD HEATER | SUMMER | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK TEMPERATURE CONTROL OPERATION
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK COOL DOWN/HEAT UP TIME
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK FAN OPERATION
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK OPERATING TEMPERATURE OF REFRIGERATION SYSTEM
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK CONDITION OF COIL
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK REFRIGERANT CHARGE
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK CONTACT POINT
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] MEG/OHM MOTOR (10 HP OR LARGER)
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK CALIBRATION OF TEMPERATURE CONTROL
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] INSPECT FAN BLADE AND SUPPORT
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] RUN CHAMBER TEMPERATURE FROM MAXIMUM TO MINIMUM
EC | ENVIRONMENTAL CHAMBER | FALL | AND LOG SWING TIMES
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] COMPARE LOGGED TIMES WITH PREVIOUS RECORDED DATA FOR
EC | ENVIRONMENTAL CHAMBER | FALL | ANY PERFORMANCE CHANGES
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] RECORD VOLTAGES AND AMPERAGES WHERE APPLICABLE
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CLEAN CONDENSER SURFACES AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] OIL FANS AND MOTORS AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK HOT GAS BYPASS AND CONDENSER PRESSURE REGULATOR
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK DISCHARGE LINE TEMPERATURES
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK CONTACTORS & RELAYS FOR WEAR & PROPER OPERATION
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] CHECK SIGHT GLASS IF APPLICABLE
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] SEMIHERMETIC COMPRESSORS CHECK OIL LEVEL AND
EC | ENVIRONMENTAL CHAMBER | FALL | PRESSURE SWITCHES
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] VERIFY INDEPENDENT OPERATION OF COOL DOWN AND
EC | ENVIRONMENTAL CHAMBER | FALL | WARM UP OPERATIONS
EC | ENVIRONMENTAL CHAMBER | FALL | [ ] PROVIDE ANNUAL CALIBRATION AND REPORT
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK TEMPERATURE CONTROL OPERATION
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK COOL DOWN/HEAT UP TIME
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK FAN OPERATION
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK OPERATING TEMPERATURES OF REFRIGERATION SYSTEM
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK CONDITION OF COIL
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK REFRIGERANT CHARGE
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] RUN CHAMBER TEMPERATURES FROM MAXIMUM TO MINIMUM AND
EC | ENVIRONMENTAL CHAMBER | WINTER | LOG SWING TIMES.
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] COMPARE LOGGED TIMES WITH PREVIOUS RECORDED DATA FOR
EC | ENVIRONMENTAL CHAMBER | WINTER | PERFORMANCE CHANGES.
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] RECORD VOLTAGES AND AMPERAGES WHERE APPLICABLE
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CLEAN CONDENSER SURFACES AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] OIL FANS AND MOTORS AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK HOT GAS BYPASS AND CONDENSER PRESSURE REGULATOR
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK DISCHARGE LINE TEMPERATURES
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK CONTACTORS AND RELAYS FOR WEAR AND
EC | ENVIRONMENTAL CHAMBER | WINTER | PROPER OPERATON
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] CHECK SIGHT GLASS IF APPLICABLE
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] SEMIHERMETIC COMPRESSORS CHECK OIL LEVEL AND
EC | ENVIRONMENTAL CHAMBER | WINTER | PRESSURE SWITCHES
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] VERIFY INDEPENDENT OPERATION OF COOL DOWN AND
EC | ENVIRONMENTAL CHAMBER | WINTER | WARM UP OPERATIONS
EC | ENVIRONMENTAL CHAMBER | WINTER | [ ] PROVIDE ANNUAL CALIBRATION AND REPORT
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK TEMPERATURE CONTROL OPERATION
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK COOL DOWN/HEAT UP TIME
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK FAN OPERATION
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK OPERATING TEMPERATURES OF REFRIGERATION SYSTEM
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK CONDITION OF COIL
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK REFRIGERANT CHARGE
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] RUN CHAMBER TEMPERATURES FOR MAXIMUM TO MINIMUM AND
EC | ENVIRONMENTAL CHAMBER | SPRING | LOG SWING TIMES
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] COMPARE LOGGED TIMES WITH PREVIOUS RECORDED DATA FOR
EC | ENVIRONMENTAL CHAMBER | SPRING | ANY PERFORMANCE CHANGES
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] RECORD VOLTAGES AND AMPERAGES WHERE APPLICABLE
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CLEAN CONDENSER SURFACES AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] OIL FANS AND MOTORS AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK HOT GAS BYPASS AND CONDENSER PRESSURE REGULATOR
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK DISCHARGE LINE TEMPERATURES
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK CONTACTORS AND RELAYS FOR WEAR AND
EC | ENVIRONMENTAL CHAMBER | SPRING | PROPER OPERATION
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] CHECK SIGHT GLASS IF APPLICABLE
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] SEMIHERMETIC COMPRESSORS CHECK OIL LEVEL
EC | ENVIRONMENTAL CHAMBER | SPRING | AND PRESSURE SWITCHES
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] VERIFY INDEPENDENT OPERATION OF COOL DOWN AND
EC | ENVIRONMENTAL CHAMBER | SPRING | WARM UP OPERATIONS
EC | ENVIRONMENTAL CHAMBER | SPRING | [ ] PROVIDE ANNUAL CALIBRATION AND REPORT
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK TEMPERATURE CONTROL OPERATION
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK COOL DOWN/ HEAT UP TIME
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK FAN OPERATION
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK OPERATING TEMPERATURE OF REFRIGERATION SYSTEM
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK CONDITION OF COIL
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK REFRIGERANT CHARGE
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] RUN CHAMBER TEMPERATURES FROM MAXIMUM TO MINIMUM AND
EC | ENVIRONMENTAL CHAMBER | SUMMER | LOG SWING TIMES
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] COMPARE LOGGED TIMES WITH PREVIOUS RECORDED DATA AND
EC | ENVIRONMENTAL CHAMBER | SUMMER | FOR ANY PERFORMANCE CHANGES
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] RECORD VOLTAGES AND AMPERAGES WHERE APPLICABLE
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CLEAN CONDENSER SURFACES AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] OIL FANS AND MOTORS AS REQUIRED
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK HOT GAS BYPASS AND CONDENSER PRESSURE REGULATOR
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK DISCHARGE LINE TEMPERATURES
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK CONTACTORS AND RELAYS FOR WEAR AND
EC | ENVIRONMENTAL CHAMBER | SUMMER | PROPER OPERATION
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] CHECK SIGHT GLASS IF APPLICABLE
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] SEMIHERMETIC COMPRESSORS CHECK OIL LEVEL AND
EC | ENVIRONMENTAL CHAMBER | SUMMER | PRESSURE SWITCHES
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] VERIFY INDEPENDENT OPERATION OF COOL DOWN AND
EC | ENVIRONMENTAL CHAMBER | SUMMER | WARM UP OPERATIONS
EC | ENVIRONMENTAL CHAMBER | SUMMER | [ ] PROVIDE ANNUAL CALIBRATION AND REPORT
EF | EXHAUST FAN | FALL | [ ] CHECK BELTS
EF | EXHAUST FAN | FALL | [ ] CHECK BELT ALIGNMENT
EF | EXHAUST FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EF | EXHAUST FAN | FALL | [ ] CHECK PULLEY WEAR
EF | EXHAUST FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
EF | EXHAUST FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EF | EXHAUST FAN | FALL | [ ] CHECK OPERATION
EF | EXHAUST FAN | WINTER | [ ] CHECK BELTS
EF | EXHAUST FAN | WINTER | [ ] CHECK BELT ALIGNMENT
EF | EXHAUST FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATIONS AND NOISE
EF | EXHAUST FAN | WINTER | [ ] CHECK OPERATION
EF | EXHAUST FAN | SPRING | [ ] CHECK BELTS
EF | EXHAUST FAN | SPRING | [ ] CHECK BELT ALIGNMENT
EF | EXHAUST FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EF | EXHAUST FAN | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EF | EXHAUST FAN | SPRING | [ ] CHECK OPERATION
EF | EXHAUST FAN | SPRING | ON ALL THREE PHASE MOTORS:
EF | EXHAUST FAN | SPRING | [ ] CHECK AMPS L1_____L2_____L3_____
EF | EXHAUST FAN | SPRING | [ ] CHECK VOLTAGE L1_____L2_____L3_____
EF | EXHAUST FAN | SUMMER | [ ] CHECK BELTS
EF | EXHAUST FAN | SUMMER | [ ] CHECK BELT ALIGNMENT
EF | EXHAUST FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EF | EXHAUST FAN | SUMMER | [ ] CHECK OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK CONTACTOR POINTS
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK THERMOSTAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK FAN OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK HEAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK TEMPERATURE RISE____________DEG F.
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK BELT IF REQUIRED
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK PULLEY WEAR
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK FAN SWITCH
EFA | ELECTRIC FORCED AIR FURNACE | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK THERMOSTAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK FAN OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK HEAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK TEMPERATURE RISE_________________DEG F
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK BELT IF EQUIPPED
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK PULLEY WEAR
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK FAN SWITCH
EFA | ELECTRIC FORCED AIR FURNACE | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK THERMOSTAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK FAN OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK HEAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK TEMPERATURE RISE_____________DEG F.
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK BELT IF EQUIPPED
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK PULLEY WEAR
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK FAN SWITCH
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
EFA | ELECTRIC FORCED AIR FURNACE | SPRING | [ ] LUBRICATE BLOWER BEARINS (PER MFG SPECS)
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK THERMOSTAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK FAN OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK HEAT OPERATION
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK TEMPERATURE RISE___________DEG F
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK BELT IF EQUIPPED
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK PULLEY WEAR
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK FAN SWITCH
EFA | ELECTRIC FORCED AIR FURNACE | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EM | ECONOMY MAINTENANCE | FALL | [ ] CHECK THE BELTS
EM | ECONOMY MAINTENANCE | FALL | [ ] CHECK FOR UNUSUAL VIBRATION
EM | ECONOMY MAINTENANCE | FALL | [ ] CHECK FOR UNUSUAL NOISE
EM | ECONOMY MAINTENANCE | FALL | [ ] VISUAL AND AUDIO CHECK
EM | ECONOMY MAINTENANCE | WINTER | [ ] CHECK THE BELTS
EM | ECONOMY MAINTENANCE | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION
EM | ECONOMY MAINTENANCE | WINTER | [ ] CHECK FOR UNUSUAL NOISE
EM | ECONOMY MAINTENANCE | WINTER | [ ] VISUAL AND AUDIO CHECK
EM | ECONOMY MAINTENANCE | SPRING | [ ] CHECK THE BELTS
EM | ECONOMY MAINTENANCE | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION
EM | ECONOMY MAINTENANCE | SPRING | [ ] CHECK FOR UNUSUAL NOISE
EM | ECONOMY MAINTENANCE | SPRING | [ ] VISUAL AND AUDIO CHECK
EM | ECONOMY MAINTENANCE | SUMMER | [ ] CHECK THE BELTS
EM | ECONOMY MAINTENANCE | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION
EM | ECONOMY MAINTENANCE | SUMMER | [ ] CHECK FOR UNUSUAL NOISE
EM | ECONOMY MAINTENANCE | SUMMER | [ ] VISUAL AND AUDIO CHECK
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK BELTS
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK PULLEY ALIGNMENT
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK PULLEY WEAR
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | FALL | DUCT HEATER
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK SEQUENCE OF OPERATION
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK VOLTAGE_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK AMPS_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK TEMPERATURE____________DEG F.
EPF | ELEVATOR PRESSURIZATION FAN | FALL | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK BELTS
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK PULLEY ALIGNMENT
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK PULLEY WEAR
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | DUCT HEATER
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK SEQUENCE OF OPERATION
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK VOLTAGE_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK AMPS_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK TEMPERATURE____________DEG F.
EPF | ELEVATOR PRESSURIZATION FAN | WINTER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK BELTS
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK PULLEY ALIGNMENT
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK PULLEY WEAR
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | DUCT HEATER
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK SEQUENCE OF OPERATION
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK VOLTAGE_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK AMPS_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK TEMPERATURE____________DEG F.
EPF | ELEVATOR PRESSURIZATION FAN | SPRING | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK BELTS
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK PULLEY ALIGNMENT
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK PULLEY WEAR
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | DUCT HEATER
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK VOLTAGE_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK AMPS_______,_______,_______
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK TEMPERATURE____________DEG F.
EPF | ELEVATOR PRESSURIZATION FAN | SUMMER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
EV | EVAPORATOR | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
EV | EVAPORATOR | FALL | [ ] ADD PAN TABLETS
EV | EVAPORATOR | FALL | [ ] INSPECT CONDENSATE PAN
EV | EVAPORATOR | FALL | [ ] INSPECT CONDITION OF COIL
EV | EVAPORATOR | FALL | [ ] CLEAN CONDENSATE TRAP
EV | EVAPORATOR | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
EV | EVAPORATOR | WINTER | [ ] ADD PAN TABLETS
EV | EVAPORATOR | WINTER | [ ] INSPECT CONDENSATE PAN
EV | EVAPORATOR | WINTER | [ ] INSPECT CONDITION OF COIL
EV | EVAPORATOR | WINTER | [ ] CLEAN CONDENSATE TRAP
EV | EVAPORATOR | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURES
EV | EVAPORATOR | SPRING | [ ] ADD PAN TABLETS
EV | EVAPORATOR | SPRING | [ ] INSPECT CONDENSATE PAN
EV | EVAPORATOR | SPRING | [ ] INSPECT CONDITION OF COIL
EV | EVAPORATOR | SPRING | [ ] CLEAN CONDENSATE TRAP
EV | EVAPORATOR | SPRING | [ ] CHECK SUPERHEAT
EV | EVAPORATOR | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
EV | EVAPORATOR | SUMMER | [ ] ADD PAN TABLETS
EV | EVAPORATOR | SUMMER | [ ] INSPECT CONDENSATE PAN
EV | EVAPORATOR | SUMMER | [ ] INSPECT CONDITION OF COIL
EV | EVAPORATOR | SUMMER | [ ] CLEAN CONDENSATE TRAP
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK THERMOSTAT SETTINGS
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK OPERATION OF HEAT ELEMENTS
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK PRESSURE RELIEF
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK VOLTAGE______________
EWH | ELECTRIC WATER HEATER | FALL | [ ] CHECK AMPS_________________
EWH | ELECTRIC WATER HEATER | WINTER | [ ] CHECK THERMOSTAT SETTINGS
EWH | ELECTRIC WATER HEATER | WINTER | [ ] CHECK OPERATION OF HEAT ELEMENTS
EWH | ELECTRIC WATER HEATER | WINTER | [ ] CHECK PRESSURE RELIEF
EWH | ELECTRIC WATER HEATER | SPRING | [ ] CHECK THERMOSTAT SETTING
EWH | ELECTRIC WATER HEATER | SPRING | [ ] CHECK OPERATION OF HEAT ELEMENTS
EWH | ELECTRIC WATER HEATER | SPRING | [ ] CHECK PRESSURE RELIEF
EWH | ELECTRIC WATER HEATER | SUMMER | [ ] CHECK THERMOSTAT SETTING
EWH | ELECTRIC WATER HEATER | SUMMER | [ ] CHECK OPERATION OF HEAT ELEMENTS
EWH | ELECTRIC WATER HEATER | SUMMER | [ ] CHECK PRESSURE RELIEF
EXT | EXPANSION TANK | FALL | [ ] CHECK AIR PRESSURE____________________PSI
EXT | EXPANSION TANK | FALL | [ ] CHECK FOR LEAKS
EXT | EXPANSION TANK | FALL | [ ] CHECK WATER LEVEL_______________% FULL
EXT | EXPANSION TANK | WINTER | [ ] CHECK FOR LEAKS
EXT | EXPANSION TANK | WINTER | [ ] CHECK WATER LEVEL__________________% FULL
EXT | EXPANSION TANK | SPRING | [ ] CHECK FOR LEAKS
EXT | EXPANSION TANK | SPRING | [ ] CHECK WATER LEVEL__________________% FULL
EXT | EXPANSION TANK | SUMMER | [ ] CHECK FOR LEAKS
EXT | EXPANSION TANK | SUMMER | [ ] CHECK WATER LEVEL______________ % FULL
FC | FLUID COOLER | FALL | [ ] CHECK VOLTAGE_____________________
FC | FLUID COOLER | FALL | [ ] CHECK FAN AMP DRAW___________________
FC | FLUID COOLER | FALL | [ ] CHECK TEMPERATURE CONTROL OPERATION
FC | FLUID COOLER | FALL | [ ] CHECK FAN OPERATION
FC | FLUID COOLER | FALL | [ ] INSPECT CONDITION OF COIL
FC | FLUID COOLER | FALL | [ ] INSPECT EXPANSION TANK
FC | FLUID COOLER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FC | FLUID COOLER | FALL | [ ] CHECK FAN BLADES FOR CRACKS
FC | FLUID COOLER | FALL | [ ] CHECK GLYCOL CONCENTRATION
FC | FLUID COOLER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
FC | FLUID COOLER | FALL | [ ] CHECK CONTACTOR POINTS
FC | FLUID COOLER | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
FC | FLUID COOLER | WINTER | [ ] CHECK VOLTAGE___________________
FC | FLUID COOLER | WINTER | [ ] CHECK FAN AMP DRAW_______________
FC | FLUID COOLER | WINTER | [ ] CHECK TEMPERATURE CONTROL OPERATION
FC | FLUID COOLER | WINTER | [ ] CHECK FAN OPERATION
FC | FLUID COOLER | WINTER | [ ] INSPECT CONDITION OF COIL
FC | FLUID COOLER | WINTER | [ ] INSPECT EXPANSION TANK
FC | FLUID COOLER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FC | FLUID COOLER | WINTER | [ ] CHECK FAN BLADES FOR CRACKS
FC | FLUID COOLER | SPRING | [ ] CHECK VOLTAGE__________________
FC | FLUID COOLER | SPRING | [ ] CHECK FAN AMP DRAW_________________
FC | FLUID COOLER | SPRING | [ ] CHECK TEMPERATURE CONTROL OPERATION
FC | FLUID COOLER | SPRING | [ ] CHECK FAN OPERATION
FC | FLUID COOLER | SPRING | [ ] INSPECT CONDITION OF COIL
FC | FLUID COOLER | SPRING | [ ] INSPECT EXPANSION TANK
FC | FLUID COOLER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FC | FLUID COOLER | SPRING | [ ] CHECK FAN BLADES FOR CRACKS
FC | FLUID COOLER | SUMMER | [ ] CHECK VOLTAGE_________________-
FC | FLUID COOLER | SUMMER | [ ] CHECK FAN AMP DRAW__________________
FC | FLUID COOLER | SUMMER | [ ] CHECK TEMPERATURE CONTROL OPERATION
FC | FLUID COOLER | SUMMER | [ ] CHECK FAN OPERATION
FC | FLUID COOLER | SUMMER | [ ] INSPECT CONDITION OF COIL
FC | FLUID COOLER | SUMMER | [ ] INSPECT EXPANSION TANK
FC | FLUID COOLER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FC | FLUID COOLER | SUMMER | [ ] CHECK FAN BLADES FOR CRACKS
FCU | FAN COIL UNIT | FALL | [ ] CHECK CONDITION OF COIL
FCU | FAN COIL UNIT | FALL | [ ] CHECK THERMOSTAT OPERATION
FCU | FAN COIL UNIT | FALL | [ ] CHECK FAN OPERATION
FCU | FAN COIL UNIT | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
FCU | FAN COIL UNIT | FALL | [ ] INSPECT CONDENSATE PAN
FCU | FAN COIL UNIT | FALL | [ ] CHECK CONDENSATE DRAIN
FCU | FAN COIL UNIT | FALL | [ ] ADD PAN TABLETS IF REQUIRED
FCU | FAN COIL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FCU | FAN COIL UNIT | FALL | [ ] LUBRICATE FAN MOTOR (PER MFG SPECS)
FCU | FAN COIL UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
FCU | FAN COIL UNIT | WINTER | [ ] CHECK CONDITION OF COIL
FCU | FAN COIL UNIT | WINTER | [ ] CHECK THERMOSTAT OPERATION
FCU | FAN COIL UNIT | WINTER | [ ] CHECK FAN OPERATION
FCU | FAN COIL UNIT | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
FCU | FAN COIL UNIT | WINTER | [ ] INSPECT CONDENSATE PAN
FCU | FAN COIL UNIT | WINTER | [ ] CHECK CONDENSATE DRAIN
FCU | FAN COIL UNIT | WINTER | [ ] ADD PAN TABLETS IF REQUIRED
FCU | FAN COIL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FCU | FAN COIL UNIT | SPRING | [ ] CHECK CONDITION OF COIL
FCU | FAN COIL UNIT | SPRING | [ ] CHECK THERMOSTAT OPERATION
FCU | FAN COIL UNIT | SPRING | [ ] CHECK FAN OPERATION
FCU | FAN COIL UNIT | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURES
FCU | FAN COIL UNIT | SPRING | [ ] INSPECT CONDENSATE PAN
FCU | FAN COIL UNIT | SPRING | [ ] ADD PAN TABLETS IF REQUIRED
FCU | FAN COIL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FCU | FAN COIL UNIT | SPRING | [ ] CHECK CONDENSATE DRAIN
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK CONDITION OF COIL
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK THERMOSTAT OPERATION
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK FAN OPERATION
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
FCU | FAN COIL UNIT | SUMMER | [ ] INSPECT CONDENSATE PAN
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK CONDENSATE DRAIN
FCU | FAN COIL UNIT | SUMMER | [ ] ADD PAN TABLETS IF REQUIRED
FCU | FAN COIL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FD | FLOOR DRAIN | FALL | [ ] INSPECT DRAIN FOR OBSTRUCTION
FD | FLOOR DRAIN | FALL | [ ] CLEAN DRAIN OBSTRUCTION
FD | FLOOR DRAIN | FALL | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
FD | FLOOR DRAIN | WINTER | [ ] INSPECT DRAIN FOR OBSTRUCTION
FD | FLOOR DRAIN | WINTER | [ ] CLEAN DRAIN OBSTRUCTION
FD | FLOOR DRAIN | WINTER | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
FD | FLOOR DRAIN | SPRING | [ ] INSPECT DRAIN FOR OBSTRUCTION
FD | FLOOR DRAIN | SPRING | [ ] CLEAN DRAIN OBSTRUCTION
FD | FLOOR DRAIN | SPRING | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
FD | FLOOR DRAIN | SUMMER | [ ] INSPECT DRAIN FOR OBSTRUCTION
FD | FLOOR DRAIN | SUMMER | [ ] CLEAN DRAIN OF OBSTRUCTION
FD | FLOOR DRAIN | SUMMER | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
FDMP | FIRE DAMPER | FALL | [ ] CHECK FUSE LINK
FDMP | FIRE DAMPER | FALL | [ ] CHECK CLEANLINESS - CLEAN IF NECESSARY
FDMP | FIRE DAMPER | FALL | [ ] CHECK DAMPER MOTOR LINKAGE IF ANY
FDMP | FIRE DAMPER | FALL | [ ] CHECK DAMPER MOTOR SPRING RETURN
FDMP | FIRE DAMPER | FALL | [ ] CHECK FOR PROPER SEAL
FDMP | FIRE DAMPER | WINTER | [ ] CHECK FUSE LINK
FDMP | FIRE DAMPER | WINTER | [ ] CHECK CLEANLINESS - CLEAN IF NECESSARY
FDMP | FIRE DAMPER | WINTER | [ ] CHECK DAMPER MOTOR LINKAGE IF ANY
FDMP | FIRE DAMPER | WINTER | [ ] CHECK DAMPER MOTOR SPRING RETURN
FDMP | FIRE DAMPER | WINTER | [ ] CHECK FOR PROPER SEAL
FDMP | FIRE DAMPER | SPRING | [ ] CHECK FUSE LINK
FDMP | FIRE DAMPER | SPRING | [ ] CHECK CLEANLINESS - CLEAN IF NECESSARY
FDMP | FIRE DAMPER | SPRING | [ ] CHECK DAMPER MOTOR LINKAGE IF ANY
FDMP | FIRE DAMPER | SPRING | [ ] CHECK DAMPER MOTOR SPRING RETURN
FDMP | FIRE DAMPER | SPRING | [ ] CHECK FOR PROPER SEAL
FDMP | FIRE DAMPER | SUMMER | [ ] CHECK FUSE LINK
FDMP | FIRE DAMPER | SUMMER | [ ] CHECK CLEANLINESS - CLEAN IF NECESSARY
FDMP | FIRE DAMPER | SUMMER | [ ] CHECK DAMPER MOTOR LINKAGE IF ANY
FDMP | FIRE DAMPER | SUMMER | [ ] CHECK DAMPER MOTOR SPRING RETURN
FDMP | FIRE DAMPER | SUMMER | [ ] CHECK FOR PROPER SEAL
FI | FIRST INSPECTION | FALL | [ ] AIR CONDITIONER
FI | FIRST INSPECTION | FALL | [ ] HEAT PUMP
FI | FIRST INSPECTION | FALL | [ ] CONDENSER UNIT (W/COMPRESSOR)
FI | FIRST INSPECTION | FALL | [ ] CONDENSER UNIT (W/O COMPRESSOR)
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] BLOWER SECTION [ ] AIR HANDLER
FI | FIRST INSPECTION | FALL | [ ] CHECK BELTS & INSPECT BLOWER FOR DIRT
FI | FIRST INSPECTION | FALL | [ ] CHECK PULLEY ALIGNMENT & CONDITION
FI | FIRST INSPECTION | FALL | [ ] CHECK CONDENSATE PAN, PUMP AND TRAP
FI | FIRST INSPECTION | FALL | [ ] ADD PAN TABS
FI | FIRST INSPECTION | FALL | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
FI | FIRST INSPECTION | FALL | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
FI | FIRST INSPECTION | FALL | [ ] CHECK SUPPLY VOLTAGE
FI | FIRST INSPECTION | FALL | [ ] CHECK MOTOR AMPS
FI | FIRST INSPECTION | FALL | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | FALL | [ ] CHECK RELIEF DAMPERS
FI | FIRST INSPECTION | FALL | [ ] CHECK CONTROL SET POINTS
FI | FIRST INSPECTION | FALL | [ ] CHECK CRANKCASE HEATER
FI | FIRST INSPECTION | FALL | [ ] CHECK OIL LEVEL
FI | FIRST INSPECTION | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
FI | FIRST INSPECTION | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
FI | FIRST INSPECTION | FALL | [ ] CHECK INDOOR COIL
FI | FIRST INSPECTION | FALL | TEMPERATURE DROP __________ DEG F
FI | FIRST INSPECTION | FALL | [ ] CHECK COMPRESSOR DISCHARGE
FI | FIRST INSPECTION | FALL | TEMPERATURE __________ DEG F
FI | FIRST INSPECTION | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
FI | FIRST INSPECTION | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
FI | FIRST INSPECTION | FALL | [ ] CHECK ECONOMIZER OPERATION
FI | FIRST INSPECTION | FALL | [ ] CHECK PULLEY WEAR
FI | FIRST INSPECTION | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
FI | FIRST INSPECTION | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE
FI | FIRST INSPECTION | FALL | [ ] CHECK FRESH AIR SCREENS
FI | FIRST INSPECTION | FALL | ELECTRIC HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | FALL | [ ] CHECK AMP DRAW (IN SEASON)
FI | FIRST INSPECTION | FALL | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | FALL | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | FALL | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | GAS HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | FALL | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | FALL | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | FALL | [ ] CHECK FAN SWITCH (IN SEASON)
FI | FIRST INSPECTION | FALL | [ ] VISUALLY INSPECT BURNERS
FI | FIRST INSPECTION | FALL | [ ] VISUALLY INSPECT FLUE
FI | FIRST INSPECTION | FALL | [ ] CHECK PILOT SETTING
FI | FIRST INSPECTION | FALL | [ ] CHECK MAIN LINE GAS PRESSURE
FI | FIRST INSPECTION | FALL | [ ] CHECK MANIFOLD GAS PRESSURE
FI | FIRST INSPECTION | FALL | [ ] CHECK COMBUSTION BLOWER WHEEL
FI | FIRST INSPECTION | FALL | [ ] OIL COMBUSTION BLOWER MOTOR
FI | FIRST INSPECTION | FALL | [ ] CHECK IGNITOR
FI | FIRST INSPECTION | FALL | [ ] VISUALLY INSPECT HEAT EXCHANGER FOR CRACKS
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] CHECK REVERSING VALVE OPERATION (HEAT PUMP)
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | HYDRONIC UNITS:
FI | FIRST INSPECTION | FALL | [ ] CHECK CONDENSER WATER TEMPERATURE
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | #1 IN __________ #1 OUT __________
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | #2 IN __________ #2 OUT __________
FI | FIRST INSPECTION | FALL | [ ] BOILER
FI | FIRST INSPECTION | FALL | [ ] OIL FURNACE
FI | FIRST INSPECTION | FALL | [ ] GAS FURNACE
FI | FIRST INSPECTION | FALL | [ ] ELECTRIC FORCED AIR FURNACE
FI | FIRST INSPECTION | FALL | [ ] GAS WATER HEATER
FI | FIRST INSPECTION | FALL | [ ] ELECTRIC WATER HEATER
FI | FIRST INSPECTION | FALL | [ ] UNIT HEATER
FI | FIRST INSPECTION | FALL | [ ] WINDOW AIR CONDITIONER
FI | FIRST INSPECTION | FALL | [ ] COMPUTER ROOM AIR CONDITIONER
FI | FIRST INSPECTION | FALL | [ ] SWAMP COOLER
FI | FIRST INSPECTION | FALL | [ ] MAKE UP AIR UNIT
FI | FIRST INSPECTION | FALL | [ ] ELECTRONIC AIR CLEANER
FI | FIRST INSPECTION | FALL | [ ] HUMIDIFIER
FI | FIRST INSPECTION | FALL | [ ] DEHUMIDIFIER
FI | FIRST INSPECTION | FALL | [ ] DAMPER
FI | FIRST INSPECTION | FALL | [ ] TIME CLOCK
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] AIR COMPRESSOR
FI | FIRST INSPECTION | FALL | [ ] AIR DRIER
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] COOLING TOWER
FI | FIRST INSPECTION | FALL | [ ] SAND FILTER
FI | FIRST INSPECTION | FALL | [ ] CHEMICAL EQUIPMENT
FI | FIRST INSPECTION | FALL | [ ] BACKFLOW PREVENTER
FI | FIRST INSPECTION | FALL | [ ] PRESSURE REDUCING VALVE
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] CONDENSER WATER PUMP
FI | FIRST INSPECTION | FALL | [ ] WELL WATER PUMP
FI | FIRST INSPECTION | FALL | [ ] CHILLED WATER PUMP
FI | FIRST INSPECTION | FALL | [ ] HOT WATER PUMP
FI | FIRST INSPECTION | FALL | [ ] CONDENSATE PUMP
FI | FIRST INSPECTION | FALL | [ ] SUMP WATER PUMP
FI | FIRST INSPECTION | FALL | [ ] SEWAGE LIFT PUMP
FI | FIRST INSPECTION | FALL | [ ] DOMESTIC WATER BOOST PUMP
FI | FIRST INSPECTION | FALL | [ ] PUMP STATION
FI | FIRST INSPECTION | FALL | [ ] STEAM CONDENSATE PUMP
FI | FIRST INSPECTION | FALL | [ ] VACUUM PUMP
FI | FIRST INSPECTION | FALL | [ ] STEAM TRAP
FI | FIRST INSPECTION | FALL | [ ] STEAM COIL
FI | FIRST INSPECTION | FALL | [ ] STEAM BASEBOARD HEATER
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] SMOKE CONTROL FAN
FI | FIRST INSPECTION | FALL | [ ] SUPPLY FAN
FI | FIRST INSPECTION | FALL | [ ] EXHAUST FAN
FI | FIRST INSPECTION | FALL | [ ] RETURN FAN
FI | FIRST INSPECTION | FALL | [ ] VARIABLE SPEED DRIVE
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] ROOF DRAIN
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] WALL HEATER
FI | FIRST INSPECTION | FALL | [ ] RADIANT ELECTRIC HEATER
FI | FIRST INSPECTION | FALL | [ ] ELECTRIC BASEBOARD HEATER
FI | FIRST INSPECTION | FALL | [ ] ELECTRIC DUCT COIL
FI | FIRST INSPECTION | FALL | [ ] VAV TERMINAL UNIT
FI | FIRST INSPECTION | FALL | [ ] FAN COIL UNIT
FI | FIRST INSPECTION | FALL | [ ] FAN-POWERED TERMINAL UNIT
FI | FIRST INSPECTION | FALL | [ ] CONSTANT AIR VOLUME TERMINAL UNIT
FI | FIRST INSPECTION | FALL
FI | FIRST INSPECTION | FALL | [ ] REFRIGERATION CONDENSING UNIT
FI | FIRST INSPECTION | FALL | [ ] FLUID COOLER
FI | FIRST INSPECTION | FALL | [ ] DRY COOLER
FI | FIRST INSPECTION | FALL | [ ] DESCRIBE ANY KNOWN FALL HAZARDS______________________
FI | FIRST INSPECTION | FALL | _________________________________________________________
FI | FIRST INSPECTION | FALL | ________________________________________________________
FI | FIRST INSPECTION | FALL | [ ] DESCRIBE ANY KNOWN BIOHAZARDS________________________
FI | FIRST INSPECTION | FALL | _________________________________________________________
FI | FIRST INSPECTION | FALL | _________________________________________________________
FI | FIRST INSPECTION | FALL | [ ] DESCRIBE ANY KNOWN CONFINED SPACE HAZARDS____________
FI | FIRST INSPECTION | FALL | ______________________________________________________
FI | FIRST INSPECTION | FALL | _________________________________________________________
FI | FIRST INSPECTION | FALL | [ ] DESCRIBE ANY OTHER SAFETY ISSUES_____________________
FI | FIRST INSPECTION | FALL | _______________________________________________________
FI | FIRST INSPECTION | FALL | _________________________________________________________
FI | FIRST INSPECTION | WINTER | [ ] AIR CONDITIONER
FI | FIRST INSPECTION | WINTER | [ ] HEAT PUMP
FI | FIRST INSPECTION | WINTER | [ ] CONDENSER UNIT (W/COMPRESSOR)
FI | FIRST INSPECTION | WINTER | [ ] CONDENSER UNIT (W/O COMPRESSOR)
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] BLOWER SECTION [ ] AIR HANDLER
FI | FIRST INSPECTION | WINTER | [ ] CHECK BELTS & INSPECT BLOWER FOR DIRT
FI | FIRST INSPECTION | WINTER | [ ] CHECK PULLEY ALIGNMENT & CONDITION
FI | FIRST INSPECTION | WINTER | [ ] CHECK CONDENSATE PAN, PUMP AND TRAP
FI | FIRST INSPECTION | WINTER | [ ] ADD PAN TABS
FI | FIRST INSPECTION | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
FI | FIRST INSPECTION | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
FI | FIRST INSPECTION | WINTER | [ ] CHECK SUPPLY VOLTAGE
FI | FIRST INSPECTION | WINTER | [ ] CHECK MOTOR AMPS
FI | FIRST INSPECTION | WINTER | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | WINTER | [ ] CHECK RELIEF DAMPERS
FI | FIRST INSPECTION | WINTER | [ ] CHECK CONTROL SET POINTS
FI | FIRST INSPECTION | WINTER | [ ] CHECK CRANKCASE HEATER
FI | FIRST INSPECTION | WINTER | [ ] CHECK OIL LEVEL
FI | FIRST INSPECTION | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
FI | FIRST INSPECTION | WINTER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
FI | FIRST INSPECTION | WINTER | [ ] CHECK INDOOR COIL
FI | FIRST INSPECTION | WINTER | TEMPERATURE DROP __________ DEG F
FI | FIRST INSPECTION | WINTER | [ ] CHECK COMPRESSOR DISCHARGE
FI | FIRST INSPECTION | WINTER | TEMPERATURE __________ DEG F
FI | FIRST INSPECTION | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
FI | FIRST INSPECTION | WINTER | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
FI | FIRST INSPECTION | WINTER | [ ] CHECK ECONOMIZER OPERATION
FI | FIRST INSPECTION | WINTER | [ ] CHECK PULLEY WEAR
FI | FIRST INSPECTION | WINTER | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
FI | FIRST INSPECTION | WINTER | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE
FI | FIRST INSPECTION | WINTER | [ ] CHECK FRESH AIR SCREENS
FI | FIRST INSPECTION | WINTER | ELECTRIC HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | WINTER | [ ] CHECK AMP DRAW (IN SEASON)
FI | FIRST INSPECTION | WINTER | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | WINTER | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | WINTER | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | GAS HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | WINTER | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | WINTER | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | WINTER | [ ] CHECK FAN SWITCH (IN SEASON)
FI | FIRST INSPECTION | WINTER | [ ] VISUALLY INSPECT BURNERS
FI | FIRST INSPECTION | WINTER | [ ] VISUALLY INSPECT FLUE
FI | FIRST INSPECTION | WINTER | [ ] CHECK PILOT SETTING
FI | FIRST INSPECTION | WINTER | [ ] CHECK MAIN LINE GAS PRESSURE
FI | FIRST INSPECTION | WINTER | [ ] CHECK MANIFOLD GAS PRESSURE
FI | FIRST INSPECTION | WINTER | [ ] CHECK COMBUSTION BLOWER WHEEL
FI | FIRST INSPECTION | WINTER | [ ] OIL COMBUSTION BLOWER MOTOR
FI | FIRST INSPECTION | WINTER | [ ] CHECK IGNITOR
FI | FIRST INSPECTION | WINTER | [ ] VISUALLY INSPECT HEAT EXCHANGER FOR CRACKS
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] CHECK REVERSING VALVE OPERATION (HEAT PUMP)
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | HYDRONIC UNITS:
FI | FIRST INSPECTION | WINTER | [ ] CHECK CONDENSER WATER TEMPERATURE
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | #1 IN __________ #1 OUT __________
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | #2 IN __________ #2 OUT __________
FI | FIRST INSPECTION | WINTER | [ ] BOILER
FI | FIRST INSPECTION | WINTER | [ ] OIL FURNACE
FI | FIRST INSPECTION | WINTER | [ ] GAS FURNACE
FI | FIRST INSPECTION | WINTER | [ ] ELECTRIC FORCED AIR FURNACE
FI | FIRST INSPECTION | WINTER | [ ] GAS WATER HEATER
FI | FIRST INSPECTION | WINTER | [ ] ELECTRIC WATER HEATER
FI | FIRST INSPECTION | WINTER | [ ] UNIT HEATER
FI | FIRST INSPECTION | WINTER | [ ] WINDOW AIR CONDITIONER
FI | FIRST INSPECTION | WINTER | [ ] COMPUTER ROOM AIR CONDITIONER
FI | FIRST INSPECTION | WINTER | [ ] SWAMP COOLER
FI | FIRST INSPECTION | WINTER | [ ] MAKE UP AIR UNIT
FI | FIRST INSPECTION | WINTER | [ ] ELECTRONIC AIR CLEANER
FI | FIRST INSPECTION | WINTER | [ ] HUMIDIFIER
FI | FIRST INSPECTION | WINTER | [ ] DEHUMIDIFIER
FI | FIRST INSPECTION | WINTER | [ ] DAMPER
FI | FIRST INSPECTION | WINTER | [ ] TIME CLOCK
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] AIR COMPRESSOR
FI | FIRST INSPECTION | WINTER | [ ] AIR DRIER
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] COOLING TOWER
FI | FIRST INSPECTION | WINTER | [ ] SAND FILTER
FI | FIRST INSPECTION | WINTER | [ ] CHEMICAL EQUIPMENT
FI | FIRST INSPECTION | WINTER | [ ] BACKFLOW PREVENTER
FI | FIRST INSPECTION | WINTER | [ ] PRESSURE REDUCING VALVE
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] CONDENSER WATER PUMP
FI | FIRST INSPECTION | WINTER | [ ] WELL WATER PUMP
FI | FIRST INSPECTION | WINTER | [ ] CHILLED WATER PUMP
FI | FIRST INSPECTION | WINTER | [ ] HOT WATER PUMP
FI | FIRST INSPECTION | WINTER | [ ] CONDENSATE PUMP
FI | FIRST INSPECTION | WINTER | [ ] SUMP WATER PUMP
FI | FIRST INSPECTION | WINTER | [ ] SEWAGE LIFT PUMP
FI | FIRST INSPECTION | WINTER | [ ] DOMESTIC WATER BOOST PUMP
FI | FIRST INSPECTION | WINTER | [ ] PUMP STATION
FI | FIRST INSPECTION | WINTER | [ ] STEAM CONDENSATE PUMP
FI | FIRST INSPECTION | WINTER | [ ] VACUUM PUMP
FI | FIRST INSPECTION | WINTER | [ ] STEAM TRAP
FI | FIRST INSPECTION | WINTER | [ ] STEAM COIL
FI | FIRST INSPECTION | WINTER | [ ] STEAM BASEBOARD HEATER
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] SMOKE CONTROL FAN
FI | FIRST INSPECTION | WINTER | [ ] SUPPLY FAN
FI | FIRST INSPECTION | WINTER | [ ] EXHAUST FAN
FI | FIRST INSPECTION | WINTER | [ ] RETURN FAN
FI | FIRST INSPECTION | WINTER | [ ] VARIABLE SPEED DRIVE
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] ROOF DRAIN
FI | FIRST INSPECTION | WINTER
FI | FIRST INSPECTION | WINTER | [ ] WALL HEATER
FI | FIRST INSPECTION | WINTER | [ ] RADIANT ELECTRIC HEATER
FI | FIRST INSPECTION | WINTER | [ ] ELECTRIC BASEBOARD HEATER
FI | FIRST INSPECTION | WINTER | [ ] ELECTRIC DUCT COIL
FI | FIRST INSPECTION | WINTER | [ ] VAV TERMINAL UNIT
FI | FIRST INSPECTION | WINTER | [ ] FAN COIL UNIT
FI | FIRST INSPECTION | WINTER | [ ] FAN-POWERED TERMINAL UNIT
FI | FIRST INSPECTION | WINTER | [ ] CONSTANT AIR VOLUME TERMINAL UNIT
FI | FIRST INSPECTION | WINTER | [ ] REFRIGERATION CONDENSING UNIT
FI | FIRST INSPECTION | WINTER | [ ] REFRIGERATION CONDENSING UNIT
FI | FIRST INSPECTION | WINTER | [ ] DRY COOLER
FI | FIRST INSPECTION | WINTER | 
FI | FIRST INSPECTION | WINTER | [ ] FLUID COOLER
FI | FIRST INSPECTION | WINTER | [ ] DESCRIBE ANY KNOWN FALL HAZARDS______________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | [ ] DESCRIBE ANY KNOWN BIOHAZARDS________________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | [ ] DESCRIBE ANY KNOWN CONFINED SPACE HAZARDS____________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | WINTER | [ ] DESCRIBE ANY OTHER SAFETY HAZARDS____________________
FI | FIRST INSPECTION | WINTER | __________________________________________________________
FI | FIRST INSPECTION | SPRING | [ ] AIR CONDITIONER
FI | FIRST INSPECTION | SPRING | [ ] HEAT PUMP
FI | FIRST INSPECTION | SPRING | [ ] CONDENSER UNIT (W/COMPRESSOR)
FI | FIRST INSPECTION | SPRING | [ ] CONDENSER UNIT (W/O COMPRESSOR)
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] BLOWER SECTION [ ] AIR HANDLER
FI | FIRST INSPECTION | SPRING | [ ] CHECK BELTS & INSPECT BLOWER FOR DIRT
FI | FIRST INSPECTION | SPRING | [ ] CHECK PULLEY ALIGNMENT & CONDITION
FI | FIRST INSPECTION | SPRING | [ ] CHECK CONDENSATE PAN, PUMP AND TRAP
FI | FIRST INSPECTION | SPRING | [ ] ADD PAN TABS
FI | FIRST INSPECTION | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
FI | FIRST INSPECTION | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
FI | FIRST INSPECTION | SPRING | [ ] CHECK SUPPLY VOLTAGE
FI | FIRST INSPECTION | SPRING | [ ] CHECK MOTOR AMPS
FI | FIRST INSPECTION | SPRING | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | SPRING | [ ] CHECK RELIEF DAMPERS
FI | FIRST INSPECTION | SPRING | [ ] CHECK CONTROL SET POINTS
FI | FIRST INSPECTION | SPRING | [ ] CHECK CRANKCASE HEATER
FI | FIRST INSPECTION | SPRING | [ ] CHECK OIL LEVEL
FI | FIRST INSPECTION | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
FI | FIRST INSPECTION | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
FI | FIRST INSPECTION | SPRING | [ ] CHECK INDOOR COIL
FI | FIRST INSPECTION | SPRING | TEMPERATURE DROP __________ DEG F
FI | FIRST INSPECTION | SPRING | [ ] CHECK COMPRESSOR DISCHARGE
FI | FIRST INSPECTION | SPRING | TEMPERATURE __________ DEG F
FI | FIRST INSPECTION | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
FI | FIRST INSPECTION | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
FI | FIRST INSPECTION | SPRING | [ ] CHECK ECONOMIZER OPERATION
FI | FIRST INSPECTION | SPRING | [ ] CHECK PULLEY WEAR
FI | FIRST INSPECTION | SPRING | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
FI | FIRST INSPECTION | SPRING | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE
FI | FIRST INSPECTION | SPRING | [ ] CHECK FRESH AIR SCREENS
FI | FIRST INSPECTION | SPRING | ELECTRIC HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | SPRING | [ ] CHECK AMP DRAW (IN SEASON)
FI | FIRST INSPECTION | SPRING | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | SPRING | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | SPRING | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | GAS HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | SPRING | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | SPRING | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | SPRING | [ ] CHECK FAN SWITCH (IN SEASON)
FI | FIRST INSPECTION | SPRING | [ ] VISUALLY INSPECT BURNERS
FI | FIRST INSPECTION | SPRING | [ ] VISUALLY INSPECT FLUE
FI | FIRST INSPECTION | SPRING | [ ] CHECK PILOT SETTING
FI | FIRST INSPECTION | SPRING | [ ] CHECK MAIN LINE GAS PRESSURE
FI | FIRST INSPECTION | SPRING | [ ] CHECK MANIFOLD GAS PRESSURE
FI | FIRST INSPECTION | SPRING | [ ] CHECK COMBUSTION BLOWER WHEEL
FI | FIRST INSPECTION | SPRING | [ ] OIL COMBUSTION BLOWER MOTOR
FI | FIRST INSPECTION | SPRING | [ ] CHECK IGNITOR
FI | FIRST INSPECTION | SPRING | [ ] VISUALLY INSPECT HEAT EXCHANGER FOR CRACKS
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] CHECK REVERSING VALVE OPERATION (HEAT PUMP)
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | HYDRONIC UNITS:
FI | FIRST INSPECTION | SPRING | [ ] CHECK CONDENSER WATER TEMPERATURE
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | #1 IN __________ #1 OUT __________
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | #2 IN __________ #2 OUT __________
FI | FIRST INSPECTION | SPRING | [ ] BOILER
FI | FIRST INSPECTION | SPRING | [ ] OIL FURNACE
FI | FIRST INSPECTION | SPRING | [ ] GAS FURNACE
FI | FIRST INSPECTION | SPRING | [ ] ELECTRIC FORCED AIR FURNACE
FI | FIRST INSPECTION | SPRING | [ ] GAS WATER HEATER
FI | FIRST INSPECTION | SPRING | [ ] ELECTRIC WATER HEATER
FI | FIRST INSPECTION | SPRING | [ ] UNIT HEATER
FI | FIRST INSPECTION | SPRING | [ ] WINDOW AIR CONDITIONER
FI | FIRST INSPECTION | SPRING | [ ] COMPUTER ROOM AIR CONDITIONER
FI | FIRST INSPECTION | SPRING | [ ] SWAMP COOLER
FI | FIRST INSPECTION | SPRING | [ ] MAKE UP AIR UNIT
FI | FIRST INSPECTION | SPRING | [ ] ELECTRONIC AIR CLEANER
FI | FIRST INSPECTION | SPRING | [ ] HUMIDIFIER
FI | FIRST INSPECTION | SPRING | [ ] DEHUMIDIFIER
FI | FIRST INSPECTION | SPRING | [ ] DAMPER
FI | FIRST INSPECTION | SPRING | [ ] TIME CLOCK
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] AIR COMPRESSOR
FI | FIRST INSPECTION | SPRING | [ ] AIR DRIER
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] COOLING TOWER
FI | FIRST INSPECTION | SPRING | [ ] SAND FILTER
FI | FIRST INSPECTION | SPRING | [ ] CHEMICAL EQUIPMENT
FI | FIRST INSPECTION | SPRING | [ ] BACKFLOW PREVENTER
FI | FIRST INSPECTION | SPRING | [ ] PRESSURE REDUCING VALVE
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] CONDENSER WATER PUMP
FI | FIRST INSPECTION | SPRING | [ ] WELL WATER PUMP
FI | FIRST INSPECTION | SPRING | [ ] CHILLED WATER PUMP
FI | FIRST INSPECTION | SPRING | [ ] HOT WATER PUMP
FI | FIRST INSPECTION | SPRING | [ ] CONDENSATE PUMP
FI | FIRST INSPECTION | SPRING | [ ] SUMP WATER PUMP
FI | FIRST INSPECTION | SPRING | [ ] SEWAGE LIFT PUMP
FI | FIRST INSPECTION | SPRING | [ ] DOMESTIC WATER BOOST PUMP
FI | FIRST INSPECTION | SPRING | [ ] PUMP STATION
FI | FIRST INSPECTION | SPRING | [ ] STEAM CONDENSATE PUMP
FI | FIRST INSPECTION | SPRING | [ ] VACUUM PUMP
FI | FIRST INSPECTION | SPRING | [ ] STEAM TRAP
FI | FIRST INSPECTION | SPRING | [ ] STEAM COIL
FI | FIRST INSPECTION | SPRING | [ ] STEAM BASEBOARD HEATER
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] SMOKE CONTROL FAN
FI | FIRST INSPECTION | SPRING | [ ] SUPPLY FAN
FI | FIRST INSPECTION | SPRING | [ ] EXHAUST FAN
FI | FIRST INSPECTION | SPRING | [ ] RETURN FAN
FI | FIRST INSPECTION | SPRING | [ ] VARIABLE SPEED DRIVE
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] ROOF DRAIN
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] WALL HEATER
FI | FIRST INSPECTION | SPRING | [ ] RADIANT ELECTRIC HEATER
FI | FIRST INSPECTION | SPRING | [ ] ELECTRIC BASEBOARD HEATER
FI | FIRST INSPECTION | SPRING | [ ] ELECTRIC DUCT COIL
FI | FIRST INSPECTION | SPRING | [ ] VAV TERMINAL UNIT
FI | FIRST INSPECTION | SPRING | [ ] FAN COIL UNIT
FI | FIRST INSPECTION | SPRING | [ ] FAN-POWERED TERMINAL UNIT
FI | FIRST INSPECTION | SPRING | [ ] CONSTANT AIR VOLUME TERMINAL UNIT
FI | FIRST INSPECTION | SPRING
FI | FIRST INSPECTION | SPRING | [ ] REFRIGERATION CONDENSING UNIT
FI | FIRST INSPECTION | SPRING | [ ] FLUID COOLER
FI | FIRST INSPECTION | SPRING | [ ] DRY COOLER
FI | FIRST INSPECTION | SPRING | [ ] DESCRIBE ANY KNOWN FALL HAZARDS______________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | [ ] DESCRIBE ANY KNOWN BIOHAZARDS________________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | [ ] DESCRIBE ANY KNOWN CONFINED SPACE HAZARDS____________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | [ ] DESCRIBE ANY OTHER SAFETY HAZARDS____________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SPRING | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | [ ] AIR CONDITIONER
FI | FIRST INSPECTION | SUMMER | [ ] HEAT PUMP
FI | FIRST INSPECTION | SUMMER | [ ] CONDENSER UNIT (W/COMPRESSOR)
FI | FIRST INSPECTION | SUMMER | [ ] CONDENSER UNIT (W/O COMPRESSOR)
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] BLOWER SECTION [ ] AIR HANDLER
FI | FIRST INSPECTION | SUMMER | [ ] CHECK BELTS & INSPECT BLOWER FOR DIRT
FI | FIRST INSPECTION | SUMMER | [ ] CHECK PULLEY ALIGNMENT & CONDITION
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP AND TRAP
FI | FIRST INSPECTION | SUMMER | [ ] ADD PAN TABS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
FI | FIRST INSPECTION | SUMMER | [ ] CHECK SUPPLY VOLTAGE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK MOTOR AMPS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK RELIEF DAMPERS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CONTROL SET POINTS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CRANKCASE HEATER
FI | FIRST INSPECTION | SUMMER | [ ] CHECK OIL LEVEL
FI | FIRST INSPECTION | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
FI | FIRST INSPECTION | SUMMER | [ ] CHECK INDOOR COIL
FI | FIRST INSPECTION | SUMMER | TEMPERATURE DROP __________ DEG F
FI | FIRST INSPECTION | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE
FI | FIRST INSPECTION | SUMMER | TEMPERATURE __________ DEG F
FI | FIRST INSPECTION | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
FI | FIRST INSPECTION | SUMMER | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK ECONOMIZER OPERATION
FI | FIRST INSPECTION | SUMMER | [ ] CHECK PULLEY WEAR
FI | FIRST INSPECTION | SUMMER | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK FRESH AIR SCREENS
FI | FIRST INSPECTION | SUMMER | ELECTRIC HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK AMP DRAW (IN SEASON)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CONTACTOR POINTS
FI | FIRST INSPECTION | SUMMER | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | GAS HEAT: (IF EQUIPPED)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK TEMPERATURE RISE (IN SEASON)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK SEQUENCER OPERATION (IN SEASON)
FI | FIRST INSPECTION | SUMMER | [ ] CHECK FAN SWITCH (IN SEASON)
FI | FIRST INSPECTION | SUMMER | [ ] VISUALLY INSPECT BURNERS
FI | FIRST INSPECTION | SUMMER | [ ] VISUALLY INSPECT FLUE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK PILOT SETTING
FI | FIRST INSPECTION | SUMMER | [ ] CHECK MAIN LINE GAS PRESSURE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK MANIFOLD GAS PRESSURE
FI | FIRST INSPECTION | SUMMER | [ ] CHECK COMBUSTION BLOWER WHEEL
FI | FIRST INSPECTION | SUMMER | [ ] OIL COMBUSTION BLOWER MOTOR
FI | FIRST INSPECTION | SUMMER | [ ] CHECK IGNITOR
FI | FIRST INSPECTION | SUMMER | [ ] VISUALLY INSPECT HEAT EXCHANGER FOR CRACKS
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] CHECK REVERSING VALVE OPERATION (HEAT PUMP)
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | HYDRONIC UNITS:
FI | FIRST INSPECTION | SUMMER | [ ] CHECK CONDENSER WATER TEMPERATURE
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | #1 IN __________ #1 OUT __________
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | #2 IN __________ #2 OUT __________
FI | FIRST INSPECTION | SUMMER | [ ] BOILER
FI | FIRST INSPECTION | SUMMER | [ ] OIL FURNACE
FI | FIRST INSPECTION | SUMMER | [ ] GAS FURNACE
FI | FIRST INSPECTION | SUMMER | [ ] ELECTRIC FORCED AIR FURNACE
FI | FIRST INSPECTION | SUMMER | [ ] GAS WATER HEATER
FI | FIRST INSPECTION | SUMMER | [ ] ELECTRIC WATER HEATER
FI | FIRST INSPECTION | SUMMER | [ ] UNIT HEATER
FI | FIRST INSPECTION | SUMMER | [ ] WINDOW AIR CONDITIONER
FI | FIRST INSPECTION | SUMMER | [ ] COMPUTER ROOM AIR CONDITIONER
FI | FIRST INSPECTION | SUMMER | [ ] SWAMP COOLER
FI | FIRST INSPECTION | SUMMER | [ ] MAKE UP AIR UNIT
FI | FIRST INSPECTION | SUMMER | [ ] ELECTRONIC AIR CLEANER
FI | FIRST INSPECTION | SUMMER | [ ] HUMIDIFIER
FI | FIRST INSPECTION | SUMMER | [ ] DEHUMIDIFIER
FI | FIRST INSPECTION | SUMMER | [ ] DAMPER
FI | FIRST INSPECTION | SUMMER | [ ] TIME CLOCK
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] AIR COMPRESSOR
FI | FIRST INSPECTION | SUMMER | [ ] AIR DRIER
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] COOLING TOWER
FI | FIRST INSPECTION | SUMMER | [ ] SAND FILTER
FI | FIRST INSPECTION | SUMMER | [ ] CHEMICAL EQUIPMENT
FI | FIRST INSPECTION | SUMMER | [ ] BACKFLOW PREVENTER
FI | FIRST INSPECTION | SUMMER | [ ] PRESSURE REDUCING VALVE
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] CONDENSER WATER PUMP
FI | FIRST INSPECTION | SUMMER | [ ] WELL WATER PUMP
FI | FIRST INSPECTION | SUMMER | [ ] CHILLED WATER PUMP
FI | FIRST INSPECTION | SUMMER | [ ] HOT WATER PUMP
FI | FIRST INSPECTION | SUMMER | [ ] CONDENSATE PUMP
FI | FIRST INSPECTION | SUMMER | [ ] SUMP WATER PUMP
FI | FIRST INSPECTION | SUMMER | [ ] SEWAGE LIFT PUMP
FI | FIRST INSPECTION | SUMMER | [ ] DOMESTIC WATER BOOST PUMP
FI | FIRST INSPECTION | SUMMER | [ ] PUMP STATION
FI | FIRST INSPECTION | SUMMER | [ ] STEAM CONDENSATE PUMP
FI | FIRST INSPECTION | SUMMER | [ ] VACUUM PUMP
FI | FIRST INSPECTION | SUMMER | [ ] STEAM TRAP
FI | FIRST INSPECTION | SUMMER | [ ] STEAM COIL
FI | FIRST INSPECTION | SUMMER | [ ] STEAM BASEBOARD HEATER
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] SMOKE CONTROL FAN
FI | FIRST INSPECTION | SUMMER | [ ] SUPPLY FAN
FI | FIRST INSPECTION | SUMMER | [ ] EXHAUST FAN
FI | FIRST INSPECTION | SUMMER | [ ] RETURN FAN
FI | FIRST INSPECTION | SUMMER | [ ] VARIABLE SPEED DRIVE
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] ROOF DRAIN
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] WALL HEATER
FI | FIRST INSPECTION | SUMMER | [ ] RADIANT ELECTRIC HEATER
FI | FIRST INSPECTION | SUMMER | [ ] ELECTRIC BASEBOARD HEATER
FI | FIRST INSPECTION | SUMMER | [ ] ELECTRIC DUCT COIL
FI | FIRST INSPECTION | SUMMER | [ ] VAV TERMINAL UNIT
FI | FIRST INSPECTION | SUMMER | [ ] FAN COIL UNIT
FI | FIRST INSPECTION | SUMMER | [ ] FAN-POWERED TERMINAL UNIT
FI | FIRST INSPECTION | SUMMER | [ ] CONSTANT AIR VOLUME TERMINAL UNIT
FI | FIRST INSPECTION | SUMMER
FI | FIRST INSPECTION | SUMMER | [ ] REFRIGERATION CONDENSING UNIT
FI | FIRST INSPECTION | SUMMER | [ ] FLUID COOLER
FI | FIRST INSPECTION | SUMMER | [ ] DRY COOLER
FI | FIRST INSPECTION | SUMMER | [ ] DESCRIBE ANY KNOWN FALL HAZARDS______________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | [ ] DESCRIBE ANY KNOWN BIOHAZARDS________________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | [ ] DESCRIBE ANY KNOWN CONFINED SPACE HAZARDS____________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | [ ] DESRCRIBE ANY OTHER SAFETY HAZARDS___________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FI | FIRST INSPECTION | SUMMER | __________________________________________________________
FN | FOUNTAIN | FALL | [ ] DRAIN FOUNTAIN IN NOVEMBER
FN | FOUNTAIN | FALL | [ ] START FOUNTAIN IN MARCH
FN | FOUNTAIN | FALL | [ ] MONTHLY MAINTENANCE CHECKS ON FOUNTAIN IN APRIL, MAY
FN | FOUNTAIN | FALL | JUNE, JULY, AUGUST, SEPTEMBER, OCTOBER
FN | FOUNTAIN | WINTER | [ ] DRAIN FOUNTAIN IN NOVEMBER
FN | FOUNTAIN | WINTER | [ ] START FOUNTAIN IN MARCH
FN | FOUNTAIN | WINTER | [ ] MAINTENANCE CHECK ON FOUNTAIN IN APRIL, MAY, JUNE,
FN | FOUNTAIN | WINTER | JULY, AUGUST, SEPTEMBER AND OCTOBER\
FN | FOUNTAIN | SPRING | [ ] DRAIN FOUNTAIN IN NOVEMBER
FN | FOUNTAIN | SPRING | [ ] START FOUNTAIN IN MARCH
FN | FOUNTAIN | SPRING | [ ] MAINTENANCE ON FOUNTAIN IN APRIL, MAY, JUNE
FN | FOUNTAIN | SPRING | JULY, AUGUST,SEPTEMBER AND OCTOBER
FN | FOUNTAIN | SUMMER | [ ] DRAIN FOUNTAIN IN NOVEMBER
FN | FOUNTAIN | SUMMER | [ ] START FOUNTAIN IN MARCH
FN | FOUNTAIN | SUMMER | [ ] MAINTENANCE ON FOUNTAIN IN APRIL, MAY, JUNE
FN | FOUNTAIN | SUMMER | JULY, AUGUST, SEPTEMBER, AND OCTOBER
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK THERMOSTAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK FAN OPERATION
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] INSPECT DAMPER LINKAGE AND OPERAION
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] LUBRICATE FAN MOTOR (PER MFG SPECS)
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK CONTACTOR POINTS
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK HEAT OPERATIONS
FTU | FAN-POWERED TERMINAL UNIT | FALL | [ ] CHECK TEMPERATURE RISE______________DEG F
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK THERMOSTAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK FAN OPERATION
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURES
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] INSPECT DAMPER LINKAGE AND OPERATION
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] LUBRICATE FAN MOTOR (PER MFG SPECS)
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK CONTACTOR POINTS
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK HEAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | WINTER | [ ] CHECK TEMPERATURE RISE_______________DEG F
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK THERMOSTAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK FAN OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURES
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] INSPECT DAMPER LINKAGE AND OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] LUBRICATE FAN MOTOR (PER MFG SPECS)
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK HEAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SPRING | [ ] CHECK TEMPERATURE RISE___________DEG F
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK THERMOSTAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK FAN OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] INSPECT DAMPER LINKAGE AND OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] LUBRICATE FAN MOTOR (PER MFG SPECS)
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK CONTACTOR POINTS
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK HEAT OPERATION
FTU | FAN-POWERED TERMINAL UNIT | SUMMER | [ ] CHECK TEMPERATURE RISE_________________DEG F
GEN | GENERATOR | FALL | [ ] CHECK GLYCOL AND CORROSION INHIBITOR
GEN | GENERATOR | FALL | [ ] CHANGE OIL
GEN | GENERATOR | FALL | [ ] CHECK BATTERY
GEN | GENERATOR | FALL | [ ] CHECK AIR CLEANER
GEN | GENERATOR | FALL | [ ] CHECK FUEL LEVELS
GEN | GENERATOR | FALL | [ ] START GENERATOR
GEN | GENERATOR | FALL | [ ] OBTAIN NORMAL OPERATING TEMPERATURES
GEN | GENERATOR | FALL | [ ] CHECK FAN BELTS
GEN | GENERATOR | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
GEN | GENERATOR | FALL | [ ] CHECK FOR VIBRATION
GEN | GENERATOR | WINTER | [ ] CHECK OIL LEVEL
GEN | GENERATOR | WINTER | [ ] CHECK BATTERY
GEN | GENERATOR | WINTER | [ ] CHECK FUEL LEVEL
GEN | GENERATOR | WINTER | [ ] START GENERATOR
GEN | GENERATOR | WINTER | [ ] OBTAIN NORMAL OPERATING TEMPERATURES
GEN | GENERATOR | SPRING | [ ] CHECK OIL LEVEL
GEN | GENERATOR | SPRING | [ ] CHECK BATTERY
GEN | GENERATOR | SPRING | [ ] CHECK FUEL LEVEL
GEN | GENERATOR | SPRING | [ ] START GENERATOR
GEN | GENERATOR | SPRING | [ ] OBTAIN NORMAL OPERATING TEMPERATURES
GEN | GENERATOR | SUMMER | [ ] CHECK OIL LEVEL
GEN | GENERATOR | SUMMER | [ ] CHECK BATTERY
GEN | GENERATOR | SUMMER | [ ] CHECK FUEL LEVEL
GEN | GENERATOR | SUMMER | [ ] START GENERATOR
GEN | GENERATOR | SUMMER | [ ] OBTAIN NORMAL OPERATING TEMPERATURES
GF | GAS FURNACE | FALL | [ ] CHECK BLOWER WHEEL
GF | GAS FURNACE | FALL | [ ] LUBRICATE MOTORS AND BEARINGS (PER MFG SPECS)
GF | GAS FURNACE | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
GF | GAS FURNACE | FALL | [ ] CHECK TEMPERATURE RISE__________________DEG.F.
GF | GAS FURNACE | FALL | [ ] CHECK MAIN LINE GAS PRESSURE____________" W.C.
GF | GAS FURNACE | FALL | [ ] CHECK MANIFOLD GAS PRESSURE_____________" W.C.
GF | GAS FURNACE | FALL | [ ] CHECK SEQUENCE OF OPERATION
GF | GAS FURNACE | FALL | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GF | GAS FURNACE | FALL | [ ] CHECK FLAME SIZE AND COLOR
GF | GAS FURNACE | FALL | [ ] CHECK HEAT EXCHANGER FOR CRACKS
GF | GAS FURNACE | WINTER | [ ] CHECK BLOWER WHEEL
GF | GAS FURNACE | WINTER | [ ] CHECK TEMPERATURE RISE________________DEG.F.
GF | GAS FURNACE | WINTER | [ ] CHECK SEQUENCE OF OPERATION
GF | GAS FURNACE | WINTER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GF | GAS FURNACE | WINTER | [ ] CHECK FLAME SIZE AND COLOR
GF | GAS FURNACE | SPRING | [ ] CHECK BLOWER WHEEL
GF | GAS FURNACE | SPRING | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
GF | GAS FURNACE | SPRING | [ ] CHECK SEQUENCE OF OPERATION
GF | GAS FURNACE | SPRING | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GF | GAS FURNACE | SPRING | [ ] CHECK FLAME SIZE AND COLOR
GF | GAS FURNACE | SUMMER | [ ] CHECK BLOWER WHEEL
GF | GAS FURNACE | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
GF | GAS FURNACE | SUMMER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GF | GAS FURNACE | SUMMER | [ ] CHECK FLAME SIZE AND COLOR
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK BLOWER WHEELS
GFA | GAS FORCED AIR FURNACE | FALL | [ ] LUBRICATE MOTORS AND BEARINGS (PER MFG SPECS)
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK TEMPERATURE RISE__________________DEG.F.
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK MAIN GAS LINE PRESSURE_____________" W.C.
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK MANIFOLD GAS PRESSURE______________" W.C.
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK SEQUENCE OF OPERATION
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK FLAME SIZE AND COLOR
GFA | GAS FORCED AIR FURNACE | FALL | [ ] CHECK HEAT EXCHANGER FOR CRACKS
GFA | GAS FORCED AIR FURNACE | WINTER | [ ] CHECK BLOWER WHEELS
GFA | GAS FORCED AIR FURNACE | WINTER | [ ] CHECK TEMPERATURE RISE________________DEG.F.
GFA | GAS FORCED AIR FURNACE | WINTER | [ ] CHECK SEQUENCE OF OPERATION
GFA | GAS FORCED AIR FURNACE | WINTER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GFA | GAS FORCED AIR FURNACE | WINTER | [ ] CHECK FLAME SIZE AND COLOR
GFA | GAS FORCED AIR FURNACE | SPRING | [ ] CHECK BLOWER WHEELS
GFA | GAS FORCED AIR FURNACE | SPRING | [ ] CHECK TEMPERATURE RISE____________________DEG.F.
GFA | GAS FORCED AIR FURNACE | SPRING | [ ] CHECK SEQUENCE OF OPERATION
GFA | GAS FORCED AIR FURNACE | SPRING | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GFA | GAS FORCED AIR FURNACE | SPRING | [ ] CHECK FLAME SIZE AND COLOR
GFA | GAS FORCED AIR FURNACE | SUMMER | [ ] CHECK BLOWER WHEELS
GFA | GAS FORCED AIR FURNACE | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
GFA | GAS FORCED AIR FURNACE | SUMMER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
GFA | GAS FORCED AIR FURNACE | SUMMER | [ ] CHECK FLAME SIZE AND COLOR
GP | GAS PACK | FALL | [ ] CHECK BELTS
GP | GAS PACK | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
GP | GAS PACK | FALL | [ ] ADD PAN TABS
GP | GAS PACK | FALL | [ ] CHECK UNUSUAL VIBRATION/NOISE
GP | GAS PACK | FALL | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
GP | GAS PACK | FALL | [ ] CHECK SUPPLY VOLTAGE
GP | GAS PACK | FALL | [ ] CHECK MOTOR AMPS
GP | GAS PACK | FALL | [ ] CHECK ECONOMIZER OPERATION
GP | GAS PACK | FALL | [ ] CHECK RELIEF DAMPERS
GP | GAS PACK | FALL | [ ] CHECK CONTROL SET POINTS
GP | GAS PACK | FALL | [ ] CHECK CRANKCASE HEATER
GP | GAS PACK | FALL | [ ] CHECK OIL LEVEL
GP | GAS PACK | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
GP | GAS PACK | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
GP | GAS PACK | FALL | [ ] CHECK INDOOR COIL
GP | GAS PACK | FALL | TEMPERATURE DROP__________DEG.F.
GP | GAS PACK | FALL | [ ] CHECK COMPRESSOR DISCHARGE
GP | GAS PACK | FALL | TEMPERATURE____________DEG.F.
GP | GAS PACK | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
GP | GAS PACK | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
GP | GAS PACK | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
GP | GAS PACK | FALL | [ ] CHECK PULLEY WEAR
GP | GAS PACK | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
GP | GAS PACK | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
GP | GAS PACK | FALL | BINDING AND LUBE
GP | GAS PACK | FALL | [ ] CHECK FRESH AIR SCREENS
GP | GAS PACK | FALL | [ ] CHECK TEMPERATURE RISE
GP | GAS PACK | FALL | [ ] CHECK SEQUENCER OPERATION
GP | GAS PACK | FALL | [ ] CHECK CAM SWITCH
GP | GAS PACK | FALL | [ ] VISUAL INSPECTION OF BURNERS
GP | GAS PACK | FALL | [ ] VISUAL INSPECTION OF HEAT EXCHANGERS AND
GP | GAS PACK | FALL | VISUAL CHECK OF FLUE
GP | GAS PACK | FALL | [ ] CHECK PILOT SETTING
GP | GAS PACK | FALL | [ ] CHECK MAIN LINE GAS PRESSURE
GP | GAS PACK | FALL | [ ] CHECK MANIFOLD GAS PRESSURE
GP | GAS PACK | FALL | [ ] CLEAN COMBUSTION BLOWER WHEEL
GP | GAS PACK | FALL | [ ] OIL COMBUSTION BLOWER MOTOR
GP | GAS PACK | FALL | [ ] CLEAN AND ADJUST IGNITOR
GP | GAS PACK | WINTER | [ ] CHECK BELTS
GP | GAS PACK | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
GP | GAS PACK | WINTER | [ ] ADD PAN TABS
GP | GAS PACK | WINTER | [ ] CHECK UNUSUAL VIBRATION/NOISE
GP | GAS PACK | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
GP | GAS PACK | WINTER | [ ] CHECK SUPPLY VOLTAGE
GP | GAS PACK | WINTER | [ ] CHECK MOTOR AMPS
GP | GAS PACK | WINTER | [ ] CHECK ECONOMIZER OPERATION
GP | GAS PACK | WINTER | [ ] CHECK RELIEF DAMPERS
GP | GAS PACK | WINTER | [ ] CHECK CONTROL SET POINTS
GP | GAS PACK | WINTER | [ ] CHECK CRANKCASE HEATER
GP | GAS PACK | WINTER | [ ] CHECK OIL LEVEL
GP | GAS PACK | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
GP | GAS PACK | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
GP | GAS PACK | WINTER | [ ] CHECK FRESH AIR INTAKE SCREENS
GP | GAS PACK | WINTER | [ ] CHECK SEQUENCE OF OPERATON
GP | GAS PACK | SPRING | [ ] CHECK BELTS
GP | GAS PACK | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
GP | GAS PACK | SPRING | [ ] ADD PAN TABS
GP | GAS PACK | SPRING | [ ] CHECK UNUSUAL VIBRATION/NOISE
GP | GAS PACK | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
GP | GAS PACK | SPRING | [ ] CHECK SUPPLY VOLTAGE
GP | GAS PACK | SPRING | [ ] CHECK MOTOR AMPS
GP | GAS PACK | SPRING | [ ] CHECK ECONOMIZER OPERATION
GP | GAS PACK | SPRING | [ ] CHECK RELIEF DAMPERS
GP | GAS PACK | SPRING | [ ] CHECK CONTROL SET POINTS
GP | GAS PACK | SPRING | [ ] CHECK CRANKCASE HEATER
GP | GAS PACK | SPRING | [ ] CHECK OIL LEVEL
GP | GAS PACK | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
GP | GAS PACK | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
GP | GAS PACK | SPRING | [ ] OUTSIDE AIR TEMPERATURE__________DEG.F.
GP | GAS PACK | SPRING | [ ] CHECK INDOOR COIL
GP | GAS PACK | SPRING | [ ] TEMPERATURE DROP_________DEG.F.
GP | GAS PACK | SPRING | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE__________DEG.F
GP | GAS PACK | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
GP | GAS PACK | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
GP | GAS PACK | SPRING | [ ] CHECK COMPRESSOR SUCTION LINE TEMP._______DEG.F.
GP | GAS PACK | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT AND BULB
GP | GAS PACK | SPRING | [ ] CHECK CAPACITY CONTROLS
GP | GAS PACK | SPRING | [ ] CHECK OPERATING CONTROLS PRESSURE SETTING
GP | GAS PACK | SPRING | [ ] CHECK SAFETIES
GP | GAS PACK | SPRING | [ ] CHECK OPERATING PRESSURES HP________LP________
GP | GAS PACK | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
GP | GAS PACK | SPRING | [ ] CHECK CONTACTOR POINTS
GP | GAS PACK | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
GP | GAS PACK | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
GP | GAS PACK | SPRING | [ ] LUBE BLOWER MOTOR
GP | GAS PACK | SPRING | [ ] CHECK OUTDOOR FAN BLADES/SUPPORTS
GP | GAS PACK | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
GP | GAS PACK | SPRING | [ ] CHECK FRESH AIR INTAKE SCREENS
GP | GAS PACK | SPRING | [ ] CHECK VFD,INLET/DISCHARGE VANE OPERATION IF APPLICABL
GP | GAS PACK | SPRING | FOR MORE THAN ONE UNIT AND/OR ONE SYSTEM LIST
GP | GAS PACK | SPRING | TEMPERATURES AND PRESSURES BELOW.
GP | GAS PACK | SUMMER | [ ] CHECK BELTS
GP | GAS PACK | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAPS
GP | GAS PACK | SUMMER | [ ] ADD PAN TABS
GP | GAS PACK | SUMMER | [ ] CHECK UNUSUAL VIBRATION/NOISE
GP | GAS PACK | SUMMER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
GP | GAS PACK | SUMMER | [ ] CHECK SUPPLY VOLTAGE
GP | GAS PACK | SUMMER | [ ] CHECK MOTOR AMPS
GP | GAS PACK | SUMMER | [ ] CHECK ECONOMIZER OPERATION
GP | GAS PACK | SUMMER | [ ] CHECK RELIEF DAMPERS
GP | GAS PACK | SUMMER | [ ] CHECK CONTROL SET POINTS
GP | GAS PACK | SUMMER | [ ] CHECK CRANKCASE HEATER
GP | GAS PACK | SUMMER | [ ] CHECK OIL LEVEL
GP | GAS PACK | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
GP | GAS PACK | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
GP | GAS PACK | SUMMER | [ ] CHECK INDOOR COIL TEMP. DROP______DEG.F.
GP | GAS PACK | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMP_______DEG.F.
GP | GAS PACK | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
GP | GAS PACK | SUMMER | [ ] CHECK FRESH AIR INTAKE SCREENS
GWH | GAS WATER HEATER | FALL | [ ] CHECK THERMOSTAT OPERATION
GWH | GAS WATER HEATER | FALL | [ ] CHECK GAS BURNER
GWH | GAS WATER HEATER | FALL | [ ] CHECK PRESSURE RELIEF
GWH | GAS WATER HEATER | FALL | [ ] INSPECT FOR FIRE HAZARDS
GWH | GAS WATER HEATER | WINTER | [ ] CHECK THERMOSTAT OPERATION
GWH | GAS WATER HEATER | WINTER | [ ] CHECK GAS BURNER
GWH | GAS WATER HEATER | WINTER | [ ] CHECK PRESSURE RELIEF
GWH | GAS WATER HEATER | WINTER | [ ] INSPECT FOR FIRE HAZARD
GWH | GAS WATER HEATER | SPRING | [ ] CHECK THERMOSTAT OPERATION
GWH | GAS WATER HEATER | SPRING | [ ] CHECK GAS BURNER
GWH | GAS WATER HEATER | SPRING | [ ] CHECK PRESSURE RELIEF
GWH | GAS WATER HEATER | SPRING | [ ] INSPECT FOR FIRE HAZARD
GWH | GAS WATER HEATER | SUMMER | [ ] CHECK THERMOSTAT OPERATION
GWH | GAS WATER HEATER | SUMMER | [ ] CHECK GAS BURNER
GWH | GAS WATER HEATER | SUMMER | [ ] CHECK PRESSURE RELIEF
GWH | GAS WATER HEATER | SUMMER | [ ] INSPECT FOR FIRE HAZARD
HBB | HOT WATER BASEBOARD HEATER | FALL | [ ] CHECK WATER INLET TEMPERATURE_________________DEG.F.
HBB | HOT WATER BASEBOARD HEATER | FALL | [ ] CHECK TEMPERATURE CONTROL
HBB | HOT WATER BASEBOARD HEATER | FALL | [ ] CHECK WATER VALVE OPERATION
HBB | HOT WATER BASEBOARD HEATER | FALL | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
HBB | HOT WATER BASEBOARD HEATER | WINTER | [ ] CHECK WATER INLET TEMPERATURE________________DEG.F.
HBB | HOT WATER BASEBOARD HEATER | WINTER | [ ] CHECK TEMPERATURE CONTROL
HBB | HOT WATER BASEBOARD HEATER | WINTER | [ ] CHECK WATER VALVE OPERATION
HBB | HOT WATER BASEBOARD HEATER | WINTER | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
HBB | HOT WATER BASEBOARD HEATER | SPRING | [ ] CHECK WATER INLET TEMPERATURE_______________DEG.F.
HBB | HOT WATER BASEBOARD HEATER | SPRING | [ ] CHECK TEMPERATURE CONTROL
HBB | HOT WATER BASEBOARD HEATER | SPRING | [ ] CHECK WATER VALVE OPERATION
HBB | HOT WATER BASEBOARD HEATER | SPRING | [ ] CHECK FOR COMBUSTIBLES AROUND HEATER
HBB | HOT WATER BASEBOARD HEATER | SUMMER | [ ] CHECK WATER INLET TEMPERATURE________________DEG. F.
HBB | HOT WATER BASEBOARD HEATER | SUMMER | [ ] CHECK TEMPERATURE CONTROL
HBB | HOT WATER BASEBOARD HEATER | SUMMER | [ ] CHECK WATER VALVE OPERATION
HBB | HOT WATER BASEBOARD HEATER | SUMMER | [ ] CHECK FOR COMBUSTIBLES AROUNDL HEATER
HC | HOT WATER COIL | FALL | [ ] CHECK TEMPERATURE CONTROL
HC | HOT WATER COIL | FALL | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
HC | HOT WATER COIL | FALL | [ ] INSPECT CONDITION OF COIL
HC | HOT WATER COIL | FALL | [ ] CHECK HOT WATER VALVE OPERATION
HC | HOT WATER COIL | FALL | [ ] INSPECT FREEZE PROTECTION IF EQUIPPED
HC | HOT WATER COIL | WINTER | [ ] CHECK TEMPERATURE CONTROL
HC | HOT WATER COIL | WINTER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURES
HC | HOT WATER COIL | WINTER | [ ] INSPECT CONDITION OF COIL
HC | HOT WATER COIL | SPRING | [ ] CHECK TEMPERATURE CONTROL
HC | HOT WATER COIL | SPRING | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
HC | HOT WATER COIL | SPRING | [ ] INSPECT CONDITION OF COIL
HC | HOT WATER COIL | SUMMER | [ ] CHECK TEMPERATURE CONTROL
HC | HOT WATER COIL | SUMMER | [ ] CHECK SUPPLY AIR AND RETURN AIR TEMPERATURE
HC | HOT WATER COIL | SUMMER | [ ] INSPECT CONDITION OF COIL
HE | HEAT EXCHANGER | FALL | [ ] CHECK TEMPERATURE INCREASE/DECREASE_________________
HE | HEAT EXCHANGER | FALL | [ ] INSPECT FOR LEAKS
HE | HEAT EXCHANGER | WINTER | [ ] CHECK TEMPERATURE INCREASE/DECREASE_______________
HE | HEAT EXCHANGER | WINTER | [ ] INSPECT FOR LEAKS
HE | HEAT EXCHANGER | SPRING | [ ] CHECK TEMPERATURE INCREASE/DECREASE_________________
HE | HEAT EXCHANGER | SPRING | [ ] INSPECT FOR LEAKS
HE | HEAT EXCHANGER | SPRING | [ ] INSPECT HEAT EXCHANGER SURFACE
HE | HEAT EXCHANGER | SPRING | [ ] CLEAN HEAT EXCHANGER SURFACE (IF REQUIRED)
HE | HEAT EXCHANGER | SUMMER | [ ] CHECK TEMPERATURE INCREASE/DECREASE_______________
HE | HEAT EXCHANGER | SUMMER | [ ] INSPECT FOR LEAKS
HF | HEPA FILTER | FALL | [ ] CHECK PRESSURE DROP________________" WC
HF | HEPA FILTER | FALL | [ ] INSPECT FILTERS
HF | HEPA FILTER | WINTER | [ ] CHECK PRESSURE DROP_______________" WC
HF | HEPA FILTER | WINTER | [ ] INSPECT FILTERS
HF | HEPA FILTER | SPRING | [ ] CHECK PRESSURE DROP_____________" WC
HF | HEPA FILTER | SPRING | [ ] INSPECT FILTERS
HF | HEPA FILTER | SUMMER | [ ] CHECK PRESSURE DROP________________" WC
HF | HEPA FILTER | SUMMER | [ ] INSPECT FILTERS
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK BELTS
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK PULLEY ALIGNMENT
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HHP | HYDRONIC HEAT PUMP | FALL | [ ] ADD PAN TABS
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION AND NOISE
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK INDOOR / OUTDOOR COIL CONDITION
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE___________________
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK MOTOR AMPS_______________________
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK SEQUENCE OF OPERATION
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK COMPRESSOR INDOOR COIL TEMPERATURE
HHP | HYDRONIC HEAT PUMP | FALL | DROP __________DEG.F.
HHP | HYDRONIC HEAT PUMP | FALL | RISE __________DEG.F.
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK COMPRESSOR DISCHARGE
HHP | HYDRONIC HEAT PUMP | FALL | TEMPERATURE_______________DEG.F.
HHP | HYDRONIC HEAT PUMP | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HHP | HYDRONIC HEAT PUMP | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK BELTS
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK PULLEY ALIGNMENT
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] ADD PAN TABS
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE___________________
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK MOTOR AMPS_______________________
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK SEQUENCE OF OPERATION
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK COMPRESSOR INDOOR COIL TEMPERATURE
HHP | HYDRONIC HEAT PUMP | WINTER | DROP __________DEG.F.
HHP | HYDRONIC HEAT PUMP | WINTER | RISE __________DEG.F.
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK COMPRESSOR DISCHARGE
HHP | HYDRONIC HEAT PUMP | WINTER | TEMPERATURE_______________DEG.F.
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HHP | HYDRONIC HEAT PUMP | WINTER | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK BELTS
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK PULLEY ALIGNMENT
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] ADD PAN TABS
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION/NOISE
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE____________________
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK MOTOR AMPS________________________
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK SEQUENCE OF OPERATION
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK COMPRESSOR INDOOR COIL TEMPERATURE
HHP | HYDRONIC HEAT PUMP | SPRING | DROP___________DEG.F.
HHP | HYDRONIC HEAT PUMP | SPRING | RISE___________DEG.F.
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK COMPRESSOR DISCHARGE
HHP | HYDRONIC HEAT PUMP | SPRING | TEMPERATURE______________DEG.F.
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK SAFETIES (HI-PRESSURE SWITCH AND FREEZESTAT)
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK CONTACTOR POINTS
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] LUBE BLOWER MOTOR
HHP | HYDRONIC HEAT PUMP | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK BELTS
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK PULLEY ALIGNMENT
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK CONDENSATE PAN,PUMP, AND TRAP
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] ADD PAN TABS
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK INDOOR / OUTDOOR COIL CONDITION
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE____________________
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK MOTOR AMPS________________________
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK COMPRESSOR INDOOR COIL TEMPERATURE
HHP | HYDRONIC HEAT PUMP | SUMMER | DROP___________DEG.F
HHP | HYDRONIC HEAT PUMP | SUMMER | RISE___________DEG.F.
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE
HHP | HYDRONIC HEAT PUMP | SUMMER | TEMPERATURE________________DEG.F.
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HHP | HYDRONIC HEAT PUMP | SUMMER | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
HP | HEAT PUMP | FALL | [ ] CHECK BELTS
HP | HEAT PUMP | FALL | [ ] CHECK PULLEY ALIGNMENT
HP | HEAT PUMP | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HP | HEAT PUMP | FALL | [ ] ADD PAN TABS
HP | HEAT PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION/ NOISE
HP | HEAT PUMP | FALL | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HP | HEAT PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE________________
HP | HEAT PUMP | FALL | [ ] CHECK MOTOR AMPS____________________
HP | HEAT PUMP | FALL | [ ] CHECK ECONOMIZER OPERATION
HP | HEAT PUMP | FALL | [ ] CHECK RELIEF DAMPERS
HP | HEAT PUMP | FALL | [ ] CHECK CONTROL SET POINTS
HP | HEAT PUMP | FALL | [ ] CHECK CRANKCASE HEATER
HP | HEAT PUMP | FALL | [ ] CHECK OIL LEVEL
HP | HEAT PUMP | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
HP | HEAT PUMP | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
HP | HEAT PUMP | FALL | [ ] CHECK MECHANICAL HEATING SEQUENCE OPERATION
HP | HEAT PUMP | FALL | [ ] CHECK COMPRESSOR INDOOR COIL
HP | HEAT PUMP | FALL | TEMPERATURE DROP_______DEG F.
HP | HEAT PUMP | FALL | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE________DEG F.
HP | HEAT PUMP | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HP | HEAT PUMP | FALL | [ ] CHECK DEFROST CONTROL
HP | HEAT PUMP | FALL | [ ] CHECK AUXILLIARY HEAT OPERATION
HP | HEAT PUMP | FALL | [ ] VERIFY OUTDOOR FAN IS OFF IN DEFROST MODE
HP | HEAT PUMP | FALL | [ ] CHECK REVERSING VALVE OPERATION
HP | HEAT PUMP | FALL | [ ] LUBE BLOWER BEARINGS (IF APPLICABLE)
HP | HEAT PUMP | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
HP | HEAT PUMP | FALL | [ ] CHECK PULLEY WEAR
HP | HEAT PUMP | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
HP | HEAT PUMP | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
HP | HEAT PUMP | FALL | BINDING AND LUBE
HP | HEAT PUMP | FALL | [ ] CHECK FRESH AIR SCREENS
HP | HEAT PUMP | WINTER | [ ] CHECK BELTS
HP | HEAT PUMP | WINTER | [ ] CHECK PULLEY ALIGNMENT
HP | HEAT PUMP | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HP | HEAT PUMP | WINTER | [ ] ADD PAN TABS
HP | HEAT PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION/NOISE
HP | HEAT PUMP | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HP | HEAT PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE___________________
HP | HEAT PUMP | WINTER | [ ] CHECK MOTOR AMPS_______________________
HP | HEAT PUMP | WINTER | [ ] CHECK ECONOMIZER OPERATION
HP | HEAT PUMP | WINTER | [ ] CHECK RELIEF DAMPERS
HP | HEAT PUMP | WINTER | [ ] CHECK CONTROL SET POINTS
HP | HEAT PUMP | WINTER | [ ] CHECK CRANKCASE HEATER
HP | HEAT PUMP | WINTER | [ ] CHECK OIL LEVEL
HP | HEAT PUMP | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
HP | HEAT PUMP | WINTER | [ ] CHECK MECHANICAL HEATING SEQUENCE OPERATION
HP | HEAT PUMP | WINTER | [ ] CHECK INDOOR COIL TEMPERATURE RISE_______DEG.F
HP | HEAT PUMP | WINTER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE________DEG F
HP | HEAT PUMP | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HP | HEAT PUMP | WINTER | [ ] CHECK DEFROST CONTROL
HP | HEAT PUMP | WINTER | [ ] CHECK AUXILLIARY HEAT OPERATION
HP | HEAT PUMP | WINTER | [ ] VERIFY OUTDOOR FAN IS OFF IN DEFROST MODE
HP | HEAT PUMP | WINTER | [ ] CHECK REVERSING VALVE OPERATION
HP | HEAT PUMP | WINTER | [ ] CHECK FRESH AIR INTAKE SCREENS
HP | HEAT PUMP | SPRING | [ ] CHECK BELTS
HP | HEAT PUMP | SPRING | [ ] CHECK PULLEY ALIGNMENT
HP | HEAT PUMP | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HP | HEAT PUMP | SPRING | [ ] ADD PAN TABS
HP | HEAT PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION/NOISE
HP | HEAT PUMP | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HP | HEAT PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE_________________
HP | HEAT PUMP | SPRING | [ ] CHECK MOTOR AMPS_____________________
HP | HEAT PUMP | SPRING | [ ] CHECK ECONOMIZER OPERATION
HP | HEAT PUMP | SPRING | [ ] CHECK RELIEF DAMPERS
HP | HEAT PUMP | SPRING | [ ] CHECK CONTROL SET POINTS
HP | HEAT PUMP | SPRING | [ ] CHECK CRANKCASE HEATER
HP | HEAT PUMP | SPRING | [ ] CHECK OIL LEVEL
HP | HEAT PUMP | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
HP | HEAT PUMP | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
HP | HEAT PUMP | SPRING | [ ] CHECK OUTDOOR TEMPERATURE________DEG.F
HP | HEAT PUMP | SPRING | [ ] CHECK INDOOR COIL TEMPERATURE DROP_________DEG.F
HP | HEAT PUMP | SPRING | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE_______DEG F
HP | HEAT PUMP | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HP | HEAT PUMP | SPRING | [ ] CHECK COMPRESSOR SUCTION LINE TEMP. _______DEG.F.
HP | HEAT PUMP | SPRING | [ ] CHECK SUB COOLING______________DEG.F.
HP | HEAT PUMP | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT AND BULB
HP | HEAT PUMP | SPRING | [ ] CHECK REVERSING VALVE OPERATION
HP | HEAT PUMP | SPRING | [ ] LUBE BLOWER MOTOR
HP | HEAT PUMP | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
HP | HEAT PUMP | SPRING | [ ] CHECK CAPACITY CONTROLS
HP | HEAT PUMP | SPRING | [ ] CHECK SAFETIES
HP | HEAT PUMP | SPRING | [ ] CHECK OPERATING PRESSURES HP_______LP________
HP | HEAT PUMP | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
HP | HEAT PUMP | SPRING | [ ] CHECK CONTACTOR POINTS
HP | HEAT PUMP | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
HP | HEAT PUMP | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
HP | HEAT PUMP | SPRING | [ ] CHECK OUTDOOR FAN BLADES/SUPPORTS
HP | HEAT PUMP | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
HP | HEAT PUMP | SPRING | [ ] CHECK FRESH AIR INTAKE SCREENS
HP | HEAT PUMP | SPRING | FOR MORE THAN ONE UNIT AND/OR ONE SYSTEM LIST
HP | HEAT PUMP | SPRING | TEMPERATURES AND PRESSURES BELOW
HP | HEAT PUMP | SUMMER | [ ] CHECK BELTS
HP | HEAT PUMP | SUMMER | [ ] CHECK PULLEY ALIGNMENT
HP | HEAT PUMP | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
HP | HEAT PUMP | SUMMER | [ ] ADD PAN TABS
HP | HEAT PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION/NOISE
HP | HEAT PUMP | SUMMER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
HP | HEAT PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE___________________
HP | HEAT PUMP | SUMMER | [ ] CHECK MOTOR AMPS_______________________
HP | HEAT PUMP | SUMMER | [ ] CHECK ECONOMIZER OPERATION
HP | HEAT PUMP | SUMMER | [ ] CHECK RELIEF DAMPERS
HP | HEAT PUMP | SUMMER | [ ] CHECK CONTROL SET POINTS
HP | HEAT PUMP | SUMMER | [ ] CHECK CRANKCASE HEATER
HP | HEAT PUMP | SUMMER | [ ] CHECK OIL LEVEL
HP | HEAT PUMP | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
HP | HEAT PUMP | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
HP | HEAT PUMP | SUMMER | [ ] CHECK INDOOR COIL TEMPERATURE DROP___________DEG.F
HP | HEAT PUMP | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE________DEG F
HP | HEAT PUMP | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HP | HEAT PUMP | SUMMER | [ ] CHECK REVERSING VALVE OPERATION
HP | HEAT PUMP | SUMMER | [ ] CHECK FRESH AIR INTAKE SCREENS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK BELTS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK PULLEY WEAR
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK COIL CONDITION
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK SUPPLY VOLTAGE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK MOTOR AMPS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK CRANKCASE HEATER
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK OIL LEVEL
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK COOLING SEQUENCE OF OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK DISCHARGE TEMPERATURE___________DEG.F
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK SUB COOLING
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK SAFETIES
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK COOLING HEAD PRESSURE CONTROL OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK HEAD PRESSURE____________HEAT MODE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK SUCTION PRESSURE_______________HEAT MODE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] INSPECT FAN BLADES AND SUPPORTS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK SAFETY OPERATION AND SETTING
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK DEFROST CONTROL
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] VERIFY OUTDOOR FAN STOPS IN DEFROST MODE
HPCU | HEAT PUMP CONDENSING UNIT | FALL | [ ] CHECK REVERSING VALVE OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK BELTS
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK PULLEY ALIGNMENT
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK UNUSUAL VIBRATION/NOISE
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK OUTDOOR COIL CONDITION
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK SUPPLY VOLTAGE
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK MOTOR AMPS
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK CONTROL SET POINTS
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK CRANKCASE HEATER
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK OIL LEVEL
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK MECHANICAL HEATING SEQUENCE OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE_________DEG.F
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK DEFROST CONTROL
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK AUXILLIARY HEAT OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] VERIFY OUTDOOR FAN IS OFF IN DEFROST MODE
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK REVERSING VALVE OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | WINTER | [ ] CHECK COOLING HEAD PRESSURE CONTROL OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK BELTS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK PULLEY WEAR
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK COIL CONDITION
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE_______________________
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK MOTOR AMPS__________________________
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK OIL LEVEL
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK COOLING SEQUENCE OF OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK DISCHARGE TEMPERATURE_________DEG.F
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK SUB COOLING__________________________
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE__________
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK CAPACITY CONTROL
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK SAFETIES
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK DISCHARGE PRESSURE___________COOL MODE
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK SUCTION PRESSURE________________COOL MODE
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK COOLING HEAD PRESSURE CONTROL OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK CONTROL POINTS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] INSPECT FAN BLADES AND SUPPORTS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK SAFETY OPERATION AND SETTING
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] INSPECT CONTACTOR POINTS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP L1___L2___L3___
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] OIL TEST SEMI-HERMETICS
HPCU | HEAT PUMP CONDENSING UNIT | SPRING | [ ] CHECK REVERSING VALVE OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK BELTS
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK PULLEY WEAR
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK COIL CONDITION
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK SUPPLY VOLTAGE
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK MOTOR AMPS
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK OIL LEVEL
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK COOLING SEQUENCE OF OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK DISCHARGE TEMPERATURE___________DEG. F
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAK (VISUAL)
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK SUB COOLING
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK CAPACITY CONTROL
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK SAFETIES
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK DISCHARGE PRESSURE
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK SUCTION PRESSURE
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK COOLING HEAD PRESSURE CONTROL OPERATION
HPCU | HEAT PUMP CONDENSING UNIT | SUMMER | [ ] CHECK REVERSING VALVE OPERATION
HRC | HEAT RECLAIM COIL | FALL | [ ] CHECK OPERATING CYCLE
HRC | HEAT RECLAIM COIL | FALL | [ ] INSPECT CONDITION OF COIL
HRC | HEAT RECLAIM COIL | FALL | [ ] CHECK TEMPERATURE INCREASE/DECREASE
HRC | HEAT RECLAIM COIL | FALL | [ ] INSPECT FOR WATER LEAK
HRC | HEAT RECLAIM COIL | FALL | [ ] CHECK VALVE OPERATION
HRC | HEAT RECLAIM COIL | FALL | [ ] CHECK FREEZE PROTECTION CONTROL
HRC | HEAT RECLAIM COIL | FALL | [ ] CHECK GLYCOL CONCENTRATION
HRC | HEAT RECLAIM COIL | WINTER | [ ] CHECK OPERATING CYCLE
HRC | HEAT RECLAIM COIL | WINTER | [ ] INSPECT CONDITION OF COIL
HRC | HEAT RECLAIM COIL | WINTER | [ ] CHECK TEMPERATURE INCREASE/DECREASE
HRC | HEAT RECLAIM COIL | WINTER | [ ] INSPECT FOR WATER LEAK
HRC | HEAT RECLAIM COIL | SPRING | [ ] CHECK OPERATING CYCLE
HRC | HEAT RECLAIM COIL | SPRING | [ ] INSPECT CONDITION OF COIL
HRC | HEAT RECLAIM COIL | SPRING | [ ] CHECK TEMPERATURE INCREASE/DECREASE
HRC | HEAT RECLAIM COIL | SPRING | [ ] INSPECT FOR WATER LEAK
HRC | HEAT RECLAIM COIL | SUMMER | [ ] CHECK OPERATING CYCLE
HRC | HEAT RECLAIM COIL | SUMMER | [ ] INSPECT CONDITION OF COIL
HRC | HEAT RECLAIM COIL | SUMMER | [ ] CHECK TEMPERATURE INCREASE/DECREASE
HRC | HEAT RECLAIM COIL | SUMMER | [ ] INSPECT FOR WATER LEAK
HUM | HUMIDIFIER | FALL | [ ] CHECK OPERATING CYCLE
HUM | HUMIDIFIER | FALL | [ ] CHECK AUTOMATIC DRAIN
HUM | HUMIDIFIER | FALL | [ ] CHECK VOLTAGE_______________________
HUM | HUMIDIFIER | FALL | [ ] CHECK AMP DRAW_________________________
HUM | HUMIDIFIER | FALL | [ ] CHECK STEAM GENERATOR
HUM | HUMIDIFIER | FALL | [ ] CHECK HEAT ELEMENTS
HUM | HUMIDIFIER | FALL | [ ] CHECK FOR SCALE BUILD UP
HUM | HUMIDIFIER | FALL | [ ] CHECK FOR WATER LEAKS
HUM | HUMIDIFIER | FALL | [ ] CLEAN HUMIDIFIER PAN
HUM | HUMIDIFIER | FALL | [ ] CHECK ELECTRICAL
HUM | HUMIDIFIER | FALL | [ ] CHECK CONTACTOR POINTS
HUM | HUMIDIFIER | FALL | [ ] CHECK HUMIDITY CONTROL
HUM | HUMIDIFIER | WINTER | [ ] CHECK OPERATING CYCLE
HUM | HUMIDIFIER | WINTER | [ ] CHECK AUTOMATIC DRAIN
HUM | HUMIDIFIER | WINTER | [ ] CHECK VOLTAGE_______________
HUM | HUMIDIFIER | WINTER | [ ] CHECK AMP DRAW_______________
HUM | HUMIDIFIER | WINTER | [ ] CHECK STEAM GENERATOR
HUM | HUMIDIFIER | WINTER | [ ] CHECK HEAT ELEMENTS
HUM | HUMIDIFIER | WINTER | [ ] CHECK FOR SCALE BUILD UP
HUM | HUMIDIFIER | WINTER | [ ] CHECK FOR WATER LEAKS
HUM | HUMIDIFIER | WINTER | [ ] CLEAN HUMIDIFIER PAN
HUM | HUMIDIFIER | SPRING | [ ] CHECK OPERATING CYCLE
HUM | HUMIDIFIER | SPRING | [ ] CHECK AUTOMATIC DRAIN
HUM | HUMIDIFIER | SPRING | [ ] CHECK VOLTAGE___________________
HUM | HUMIDIFIER | SPRING | [ ] CHECK AMP DRAW__________________
HUM | HUMIDIFIER | SPRING | [ ] CHECK STEAM GENERATOR
HUM | HUMIDIFIER | SPRING | [ ] CHECK HEAT ELEMENTS
HUM | HUMIDIFIER | SPRING | [ ] CHECK FOR SCALE BUILD UP
HUM | HUMIDIFIER | SPRING | [ ] CHECK FOR WATER LEAKS
HUM | HUMIDIFIER | SPRING | [ ] CLEAN HUMIDIFIER PAN
HUM | HUMIDIFIER | SUMMER | [ ] CHECK OPERATING CYCLE
HUM | HUMIDIFIER | SUMMER | [ ] CHECK AUTOMATIC DRAIN
HUM | HUMIDIFIER | SUMMER | [ ] CHECK VOLTAGE__________________
HUM | HUMIDIFIER | SUMMER | [ ] CHECK AMP DRAW_________________
HUM | HUMIDIFIER | SUMMER | [ ] CHECK STEAM GENERATOR
HUM | HUMIDIFIER | SUMMER | [ ] CHECK HEAT ELEMENTS
HUM | HUMIDIFIER | SUMMER | [ ] CHECK FOR SCALE BUILD-UP
HUM | HUMIDIFIER | SUMMER | [ ] CHECK FOR WATER LEAKS
HUM | HUMIDIFIER | SUMMER | [ ] CLEAN HUMIDIFIER PAN
HVU | HEAT VENT UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HVU | HEAT VENT UNIT | FALL | [ ] CHECK BLOWER OPERATION
HVU | HEAT VENT UNIT | FALL | [ ] CHECK DAMPER OPERATION
HVU | HEAT VENT UNIT | FALL | [ ] CHECK BLOWER BELT
HVU | HEAT VENT UNIT | FALL | [ ] CHECK PULLEY WEAR
HVU | HEAT VENT UNIT | FALL | [ ] CHECK OPERATIONAL SEQUENCE
HVU | HEAT VENT UNIT | FALL | [ ] CHECK VOLTAGE___________________
HVU | HEAT VENT UNIT | FALL | [ ] CHECK AMP DRAW___________________
HVU | HEAT VENT UNIT | FALL | [ ] CHECK COMBUSTION BLOWER WHEEL AND CLEAN IF REQUIRED
HVU | HEAT VENT UNIT | FALL | [ ] CHECK DAMPER OPERATION
HVU | HEAT VENT UNIT | FALL | [ ] CHECK AIR PROVING SWITCH
HVU | HEAT VENT UNIT | FALL | [ ] CHECK TEMPERATURE CONTROL
HVU | HEAT VENT UNIT | FALL | [ ] INSPECT IGNITOR GAP
HVU | HEAT VENT UNIT | FALL | [ ] CHECK TEMPERATURE RISE
HVU | HEAT VENT UNIT | FALL | [ ] CHECK GAS MANIFOLD PRESSURE_________________" WC
HVU | HEAT VENT UNIT | FALL | [ ] CHECK MAIN LINE GAS PRESSURE_________________" WC
HVU | HEAT VENT UNIT | FALL | [ ] CHECK PILOT GAS VALVE
HVU | HEAT VENT UNIT | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
HVU | HEAT VENT UNIT | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
HVU | HEAT VENT UNIT | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK BLOWER OPERATION
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK DAMPER OPERATION
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK BLOWER BELT
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK PULLEY WEAR
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK OPERATIONAL SEQUENCE
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK VOLTAGE_______________
HVU | HEAT VENT UNIT | WINTER | [ ] CHECK AMP DRAW_______________
HVU | HEAT VENT UNIT | SPRING | [ ] LUBRICATE BLOWER BEARING (PER MFG SPECS)
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK BLOWER OPERATION
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK DAMPER OPERATION
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK BLOWER BELT
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK PULLEY WEAR
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK OPERATIONAL SEQUENCE
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK VOLTAGE__________________
HVU | HEAT VENT UNIT | SPRING | [ ] CHECK AMP DRAW_________________
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK BLOWER OPERATION
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK BLOWER BELT
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK PULLEY WEAR
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK OPERATIONAL SEQUENCE
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK VOLTAGE_________________
HVU | HEAT VENT UNIT | SUMMER | [ ] CHECK AMP DRAW_________________
HWP | HOT WATER PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
HWP | HOT WATER PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE__________________
HWP | HOT WATER PUMP | FALL | [ ] CHECK MOTOR AMPS______________________
HWP | HOT WATER PUMP | FALL | [ ] CHECK PRESSURES: DISCHARGE______________
HWP | HOT WATER PUMP | FALL | SUCTION______________
HWP | HOT WATER PUMP | FALL | [ ] CHECK FOR SEAL LEAKS
HWP | HOT WATER PUMP | FALL | [ ] CHECK MOTOR AND BEARING OIL LEVEL
HWP | HOT WATER PUMP | FALL | [ ] ALTERNATE LEAD / LAG PUMP
HWP | HOT WATER PUMP | FALL | [ ] CHECK AUTOMATIC STAND-BY CHANGE OVER
HWP | HOT WATER PUMP | FALL | [ ] LUBRICATE BEARING ASSEMBLY
HWP | HOT WATER PUMP | FALL | [ ] LUBRICATE PUMP MOTOR BEARINGS
HWP | HOT WATER PUMP | FALL | [ ] VISUALLY INSPECT COUPLING
HWP | HOT WATER PUMP | FALL | [ ] CLEAN AND INSPECT STRAINER
HWP | HOT WATER PUMP | FALL | [ ] CHECK CONTACTOR/STARTER POINTS
HWP | HOT WATER PUMP | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
HWP | HOT WATER PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
HWP | HOT WATER PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE__________________
HWP | HOT WATER PUMP | WINTER | [ ] CHECK MOTOR AMPS______________________
HWP | HOT WATER PUMP | WINTER | [ ] CHECK PRESSURES: DISCHARGE_______________
HWP | HOT WATER PUMP | WINTER | SUCTION_______________
HWP | HOT WATER PUMP | WINTER | [ ] CHECK FOR SEAL LEAKS
HWP | HOT WATER PUMP | WINTER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
HWP | HOT WATER PUMP | WINTER | [ ] ALTERNATE LEAD / LAG PUMP
HWP | HOT WATER PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
HWP | HOT WATER PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE_____________________
HWP | HOT WATER PUMP | SPRING | [ ] CHECK MOTOR AMPS_________________________
HWP | HOT WATER PUMP | SPRING | [ ] CHECK PRESSURES: DISCHARGE______________
HWP | HOT WATER PUMP | SPRING | SUCTION______________
HWP | HOT WATER PUMP | SPRING | [ ] CHECK FOR SEAL LEAKS
HWP | HOT WATER PUMP | SPRING | [ ] CHECK MOTOR AND BEARING OIL LEVEL
HWP | HOT WATER PUMP | SPRING | [ ] ALTERNATE LEAD / LAG PUMP
HWP | HOT WATER PUMP | SPRING | [ ] LUBRICATE BEARING ASSEMBLY
HWP | HOT WATER PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
HWP | HOT WATER PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE____________________
HWP | HOT WATER PUMP | SUMMER | [ ] CHECKL MOTOR AMPS_______________________
HWP | HOT WATER PUMP | SUMMER | [ ] CHECK PRESSURES: DISCHARGE______________
HWP | HOT WATER PUMP | SUMMER | SUCTION______________
HWP | HOT WATER PUMP | SUMMER | [ ] CHECK FOR SEAL LEAKS
HWP | HOT WATER PUMP | SUMMER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
HWP | HOT WATER PUMP | SUMMER | [ ] ALTERNATE LEAD / LAG PUMP
HWR | HOT WATER RADIATOR | FALL | [ ] CHECK HOT WATER VALVE OPERATION
HWR | HOT WATER RADIATOR | FALL | [ ] CHECK TEMPERATURE CONTROL
HWR | HOT WATER RADIATOR | WINTER | [ ] CHECK HOT WATER VALVE OPERATION
HWR | HOT WATER RADIATOR | WINTER | [ ] CHECK TEMPERATURE CONTROL
HWR | HOT WATER RADIATOR | SPRING | [ ] CHECK HOT WATER VALVE OPERATION
HWR | HOT WATER RADIATOR | SPRING | [ ] CHECK TEMPERATURE CONTROL
HWR | HOT WATER RADIATOR | SUMMER | [ ] CHECK HOT WATER VALVE OPERATION
HWR | HOT WATER RADIATOR | SUMMER | [ ] CHECK TEMPERATURE CONTROL
IM | ICE MACHINE | FALL | [ ] CHECK AND CLEAN CONDENSOR AND FAN
IM | ICE MACHINE | FALL | [ ] CHECK WATER COOLED CONDENSOR FLOW
IM | ICE MACHINE | FALL | [ ] CHECK SUMP FOR SLIME AND MINERAL DEPOSITS
IM | ICE MACHINE | FALL | [ ] CHECK PUMP
IM | ICE MACHINE | FALL | [ ] CHECK DISTRIBUTOR TUBES AND NOZZLES
IM | ICE MACHINE | FALL | [ ] CHECK PLATES FOR MINERAL DEPOSITS AND CLEANLINESS
IM | ICE MACHINE | FALL | [ ] CHECK CYLINDER AND AUGER FOR MINERAL DEPOSITS
IM | ICE MACHINE | FALL | [ ] CHECK AUGER BEARINGS
IM | ICE MACHINE | FALL | [ ] CHECK AND LUBE AUGER MOTOR
IM | ICE MACHINE | FALL | [ ] CHECK BELTS
IM | ICE MACHINE | FALL | [ ] CHECK GEARBOX
IM | ICE MACHINE | FALL | [ ] CHECK VOLTAGE_____________________
IM | ICE MACHINE | FALL | [ ] CHECK COMPRESSOR AMPS______________
IM | ICE MACHINE | FALL | [ ] CHECK AUGER MOTOR AMPS_____________
IM | ICE MACHINE | FALL | [ ] CHECK COMPRESSOR DISCHARGE TEMP
IM | ICE MACHINE | FALL | AT START OF FREEZING CYCLE_________________
IM | ICE MACHINE | FALL | [ ] CHECK COMPRESSOR SUCTION TEMP
IM | ICE MACHINE | FALL | NEAR END OF FREEZING CYCLE__________________
IM | ICE MACHINE | FALL | [ ] CHECK TIME FROM END OF ONE HARVEST CYCLE TO END
IM | ICE MACHINE | FALL | OF NEXT HARVEST CYCLE__________________________
IM | ICE MACHINE | WINTER | [ ] CHECK AND CLEAN CONDENSOR FAN
IM | ICE MACHINE | WINTER | [ ] CHECK WATER COOLED CONDENSOR FLOW
IM | ICE MACHINE | WINTER | [ ] CHECK SUMP FOR SLIME AND MINERAL DEPOSITS
IM | ICE MACHINE | WINTER | [ ] CHECK PUMP
IM | ICE MACHINE | WINTER | [ ] CHECK DISTRIBUTOR TUBES AND NOZZLES
IM | ICE MACHINE | WINTER | [ ] CHECK PLATES FOR MINERAL DEPOSITS AND CLEANLINESS
IM | ICE MACHINE | WINTER | [ ] CHECK CYLINDER AND AUGER FOR MINERAL DEPOSITS
IM | ICE MACHINE | WINTER | [ ] CHECK AUGER BEARINGS
IM | ICE MACHINE | WINTER | [ ] CHECK AND LUBE AUGER MOTOR
IM | ICE MACHINE | WINTER | [ ] CHECK BELT
IM | ICE MACHINE | WINTER | [ ] CHECK PULLEYS
IM | ICE MACHINE | WINTER | [ ] CHECK GEARBOX
IM | ICE MACHINE | WINTER | [ ] CHECK VOLTAGE________________________
IM | ICE MACHINE | WINTER | [ ] CHECK COMPRESSOR AMPS___________________
IM | ICE MACHINE | WINTER | [ ] CHECK AUGER MOTOR AMPS__________________
IM | ICE MACHINE | WINTER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE AT START
IM | ICE MACHINE | WINTER | OF FREEZING CYCLE______________________
IM | ICE MACHINE | WINTER | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE NEAR END OF
IM | ICE MACHINE | WINTER | FREEZING CYCLE______________________
IM | ICE MACHINE | WINTER | [ ] CHECK TIME FROM END OF ONE HARVEST CYCLE TO END OF
IM | ICE MACHINE | WINTER | NEXT HARVEST CYCLE__________________
IM | ICE MACHINE | WINTER | [ ] CHECK CUBER PRODUCTION (WEIGH ONE BATCH OF ICE TIMES
IM | ICE MACHINE | WINTER | THE NUMBER OF CYCLES PER DAY)
IM | ICE MACHINE | WINTER | [ ] CHECK FLAKER PRODUCTION (WEIGH 6 MINUTES OF
IM | ICE MACHINE | WINTER | PRODUCTION TIMES 10 TIMES 24)
IM | ICE MACHINE | SPRING | [ ] CHECK AND CLEAN CONDENSOR AND FAN
IM | ICE MACHINE | SPRING | [ ] CHECK WATER COOLED CONDENSOR FLOW
IM | ICE MACHINE | SPRING | [ ] CHECK SUMP FOR SLIME AND MINERAL DEPOSITS
IM | ICE MACHINE | SPRING | [ ] CHECK PUMP
IM | ICE MACHINE | SPRING | [ ] CHECK DISTRIBUTOR TUBES AND NOZZLES
IM | ICE MACHINE | SPRING | [ ] CHECK PLATES FOR MINERAL DEPOSITS AND CLEANLINESS
IM | ICE MACHINE | SPRING | [ ] CHECK CYLINDER AND AUGER FOR MINERAL DEPOSITS
IM | ICE MACHINE | SPRING | [ ] CHECK AUGER BEARINGS
IM | ICE MACHINE | SPRING | [ ] CHECK AND LUBE AUGER MOTOR
IM | ICE MACHINE | SPRING | [ ] CHECK BELT
IM | ICE MACHINE | SPRING | [ ] CHECK PULLEYS
IM | ICE MACHINE | SPRING | [ ] CHECK GEARBOX
IM | ICE MACHINE | SPRING | [ ] CHECK VOLTAGE___________________
IM | ICE MACHINE | SPRING | [ ] CHECK COMPRESSOR AMPS___________
IM | ICE MACHINE | SPRING | [ ] CHECK AUGER MOTOR AMPS__________
IM | ICE MACHINE | SPRING | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE AT START
IM | ICE MACHINE | SPRING | OF FREEZING CYCLE__________________________
IM | ICE MACHINE | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE NEAR END
IM | ICE MACHINE | SPRING | OF FREEZING CYCLE________________________
IM | ICE MACHINE | SPRING | [ ] CHECK TIME FROM END OF ONE HARVEST CYCLE TO END
IM | ICE MACHINE | SPRING | OF NEXT HARVEST CYCLE____________________
IM | ICE MACHINE | SUMMER | [ ] CHECK AND CLEAN CONDENSOR AND FAN
IM | ICE MACHINE | SUMMER | [ ] CHECK WATER COOLED CONDENSOR FLOW
IM | ICE MACHINE | SUMMER | [ ] CHECK SUMP FOR SLIME AND MINERAL DEPOSITS
IM | ICE MACHINE | SUMMER | [ ] CHECK PUMP
IM | ICE MACHINE | SUMMER | [ ] CHECK DISTRIBUTOR TUBES AND NOZZLES
IM | ICE MACHINE | SUMMER | [ ] CHECK PLATES FOR MINERAL DEPOSITS AND CLEANLINESS
IM | ICE MACHINE | SUMMER | [ ] CHECK CYLINDER AND AUGER FOR MINERAL DEPOSITS
IM | ICE MACHINE | SUMMER | [ ] CHECK AUGER BEARINGS
IM | ICE MACHINE | SUMMER | [ ] CHECK AND LUBE AUGER MOTOR
IM | ICE MACHINE | SUMMER | [ ] CHECK BELT
IM | ICE MACHINE | SUMMER | [ ] CHECK PULLEYS
IM | ICE MACHINE | SUMMER | [ ] CHECK GEARBOX
IM | ICE MACHINE | SUMMER | [ ] CHECK VOLTAGE_______________________
IM | ICE MACHINE | SUMMER | [ ] CHECK COMPRESSOR AMPS_______________
IM | ICE MACHINE | SUMMER | [ ] CHECK AUGER MOTOR AMPS______________
IM | ICE MACHINE | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE AT START
IM | ICE MACHINE | SUMMER | OF FREEZING CYCLE___________________
IM | ICE MACHINE | SUMMER | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE NEAR END
IM | ICE MACHINE | SUMMER | OF FREEZING CYCLE____________________________
IM | ICE MACHINE | SUMMER | [ ] CHECK TIME FROM END OF ONE HARVEST CYCLE TO END
IM | ICE MACHINE | SUMMER | OF NEXT HARVEST CYCLE________________________
IU | INDUCTION UNIT | FALL | [ ] CHECK THERMOSTAT OPERATION
IU | INDUCTION UNIT | FALL | [ ] CHECK DAMPER ACTUATOR OPERATION
IU | INDUCTION UNIT | FALL | [ ] CHECK LINKAGE
IU | INDUCTION UNIT | FALL | [ ] CHECK FAN OPERATION
IU | INDUCTION UNIT | FALL | [ ] CHECK HEAT OPERATION (IF EQUIPPED)
IU | INDUCTION UNIT | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
IU | INDUCTION UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
IU | INDUCTION UNIT | FALL | [ ] CHECK CONTACTOR POINTS
IU | INDUCTION UNIT | WINTER | [ ] CHECK THERMOSTAT OPERATION
IU | INDUCTION UNIT | WINTER | [ ] CHECK DAMPER ACTUATOR OPERATION
IU | INDUCTION UNIT | WINTER | [ ] CHECK LINKAGE
IU | INDUCTION UNIT | WINTER | [ ] CHECK FAN OPERATION
IU | INDUCTION UNIT | WINTER | [ ] CHECK HEAT OPERATION (IF EQUIPPED)
IU | INDUCTION UNIT | WINTER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
IU | INDUCTION UNIT | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
IU | INDUCTION UNIT | WINTER | [ ] CHECK CONTACTOR POINTS
IU | INDUCTION UNIT | SPRING | [ ] CHECK THERMOSTAT OPERATION
IU | INDUCTION UNIT | SPRING | [ ] CHECK DAMPER ACTUATOR OPERATION
IU | INDUCTION UNIT | SPRING | [ ] CHECK LINKAGE
IU | INDUCTION UNIT | SPRING | [ ] CHECK FAN OPERATION
IU | INDUCTION UNIT | SPRING | [ ] CHECK HEAT OPERATION (IF EQUIPPED)
IU | INDUCTION UNIT | SPRING | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
IU | INDUCTION UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
IU | INDUCTION UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
IU | INDUCTION UNIT | SUMMER | [ ] CHECK THERMOSTAT OPERATION
IU | INDUCTION UNIT | SUMMER | [ ] CHECK DAMPER ACTUATOR OPERATION
IU | INDUCTION UNIT | SUMMER | [ ] CHECK LINKAGE
IU | INDUCTION UNIT | SUMMER | [ ] CHECK FAN OPERATION
IU | INDUCTION UNIT | SUMMER | [ ] CHECK HEAT OPERATION (IF EQUIPPED)
IU | INDUCTION UNIT | SUMMER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
IU | INDUCTION UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
IU | INDUCTION UNIT | SUMMER | [ ] CHECK CONTACTOR POINTS
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check compressor oil level.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Oil level is __________ of sight glass.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check R-22 refrigerant charge. Check and record
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | color of moisture eye.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Color __________.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Leak check the system for refrigerant leaks. Make
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | sure caps and fittings are tight.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check compressor amp draws.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | L1 + L2 __________ L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | L1 + L2 __________ L2 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | L1 + L3 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check head cooling fan amps.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | L1 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check amp draws on crankcase heater.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check system pressures.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Bypass ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Pulldown ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check system temperatures
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Bypass ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Pulldown ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check oil pressure. Oil pressure is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Oil pressure differential is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check operation of low pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Cut-in ________ Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check discharge pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Record the lowest superheat at the compressor.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Superheat ________ deg F
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Record EPR settings.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Line A ________ psig Line B ________ psig
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check and verify operation of oil pressure switch.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | Time Out ________ sec.
LEC | LARGE ENVIRONMENTAL CHAMBER | FALL | [ ] Check water cooled condenser.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check compressor oil level.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Oil level is __________ of sight glass.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check R-22 refrigerant charge. Check and record
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | color of moisture eye.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Color __________.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Leak check the system for refrigerant leaks. Make
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | sure caps and fittings are tight.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check compressor amp draws.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | L1 + L2 __________ L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | L1 + L2 __________ L2 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | L1 + L3 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check head cooling fan amps.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | L1 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check amp draws on crankcase heater.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check system pressures.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Bypass ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Pulldown ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check system temperatures
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Bypass ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Pulldown ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check oil pressure. Oil pressure is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Oil pressure differential is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check operation of low pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Cut-in ________ Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check discharge pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Record the lowest superheat at the compressor.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Superheat ________ deg F
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Record EPR settings.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Line A ________ psig Line B ________ psig
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | [ ] Check and verify operation of oil pressure switch.
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER
LEC | LARGE ENVIRONMENTAL CHAMBER | WINTER | Time Out ________ sec.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check compressor oil level.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Oil level is __________ of sight glass.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check R-22 refrigerant charge. Check and record
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | color of moisture eye.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Color __________.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Leak check the system for refrigerant leaks. Make
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | sure caps and fittings are tight.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check compressor amp draws.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | L1 + L2 __________ L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | L1 + L2 __________ L2 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | L1 + L3 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check head cooling fan amps.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | L1 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check amp draws on crankcase heater.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check system pressures.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Bypass ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Pulldown ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check system temperatures
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Bypass ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Pulldown ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check oil pressure. Oil pressure is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Oil pressure differential is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check operation of low pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Cut-in ________ Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check discharge pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Record the lowest superheat at the compressor.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Superheat ________ deg F
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Record EPR settings.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Line A ________ psig Line B ________ psig
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | [ ] Check and verify operation of oil pressure switch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING
LEC | LARGE ENVIRONMENTAL CHAMBER | SPRING | Time Out ________ sec.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check compressor oil level.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Oil level is __________ of sight glass.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check R-22 refrigerant charge. Check and record
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | color of moisture eye.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Color __________.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Leak check the system for refrigerant leaks. Make
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | sure caps and fittings are tight.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check compressor amp draws.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | L1 + L2 __________ L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | L1 + L2 __________ L2 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | L1 + L3 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check head cooling fan amps.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | L1 __________ L3 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check amp draws on crankcase heater.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | L1 __________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check system pressures.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Bypass ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Pulldown ________ psig Suction ________ psig Disch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check system temperatures
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Bypass ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Pulldown ________ Suction ________ Disch. ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check oil pressure. Oil pressure is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Oil pressure differential is ________ psig.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check operation of low pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Cut-in ________ Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check discharge pressure control.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Cut-out ________
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Record the lowest superheat at the compressor.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Superheat ________ deg F
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Record EPR settings.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Line A ________ psig Line B ________ psig
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | [ ] Check and verify operation of oil pressure switch.
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER
LEC | LARGE ENVIRONMENTAL CHAMBER | SUMMER | Time Out ________ sec.
LP | LIQUID PUMP | FALL | [ ] CHECK PUMP OPERATION
LP | LIQUID PUMP | FALL | [ ] CHECK VOLTAGE_________________
LP | LIQUID PUMP | FALL | [ ] CHECK AMPS______________________
LP | LIQUID PUMP | FALL | [ ] CHECK PRESSURE_________________
LP | LIQUID PUMP | WINTER | [ ] CHECK PUMP OPERATION
LP | LIQUID PUMP | WINTER | [ ] CHECK VOLTAGE_______________
LP | LIQUID PUMP | WINTER | [ ] CHECK AMPS__________________
LP | LIQUID PUMP | WINTER | [ ] CHECK PRESSURE__________________
LP | LIQUID PUMP | SPRING | [ ] CHECK PUMP OPERATION
LP | LIQUID PUMP | SPRING | [ ] CHECK VOLTAGE______________________
LP | LIQUID PUMP | SPRING | [ ] CHECK AMPS__________________________
LP | LIQUID PUMP | SPRING | [ ] CHECK PRESSURE_______________________
LP | LIQUID PUMP | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
LP | LIQUID PUMP | SPRING | [ ] CHECK CONTACTOR POINTS
LP | LIQUID PUMP | SPRING | [ ] LUBRICATE MOTOR BEARINGS (IF REQUIRED)
LP | LIQUID PUMP | SUMMER | [ ] CHECK PUMP OPERATION
LP | LIQUID PUMP | SUMMER | [ ] CHECK VOLTAGE___________________
LP | LIQUID PUMP | SUMMER | [ ] CHECK AMPS________________________
LP | LIQUID PUMP | SUMMER | [ ] CHECK PRESSURE_____________________
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK UNUSUAL VIBRATION AND NOISE
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK SUPPLY VOLTAGE
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK MOTOR AMPS
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK GAS PRESSURES__________________________
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK FOR GAS LEAKS
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK H2O/GLYCOL LEVEL
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK FLAME SIGNAL
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK HYDROVAIRE VENTURIS
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK HYDROVAIRE GUAGES
LPB | LIQUID PROPANE BOILER | FALL | [ ] CHECK AQUAVAIRE SAFETIES
LPB | LIQUID PROPANE BOILER | FALL | [ ] RECORD ALL CUAGE READINGS
LPB | LIQUID PROPANE BOILER | FALL | ________________WATERBATH TEMPERATURE
LPB | LIQUID PROPANE BOILER | FALL | ________________PROPANE PRESSURE AT AQUAVAIRE
LPB | LIQUID PROPANE BOILER | FALL | ________________HYDROVAIRE PRESSURE
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK SUPPLY VOLTAGE
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK MOTOR AMPS
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK GAS PRESSURES__________________________
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK FOR GAS LEAKS
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK H2O/GLYCOL LEVEL
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK FLAME SIGNAL
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK HYDROVAIRE VENTURIS
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK HYDROVAIRE GUAGES
LPB | LIQUID PROPANE BOILER | WINTER | [ ] CHECK AQUAVAIRE SAFETIES
LPB | LIQUID PROPANE BOILER | WINTER | [ ] RECORD ALL CUAGE READINGS
LPB | LIQUID PROPANE BOILER | WINTER | ________________WATERBATH TEMPERATURE
LPB | LIQUID PROPANE BOILER | WINTER | ________________PROPANE PRESSURE AT AQUAVAIRE
LPB | LIQUID PROPANE BOILER | WINTER | ________________HYDROVAIRE PRESSURE
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK UNUSUAL VIBRATION AND NOISE
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK SUPPLY VOLTAGE
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK MOTOR AMPS
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK GAS PRESSURES__________________________
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK FOR GAS LEAKS
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK H2O/GLYCOL LEVEL
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK FLAME SIGNAL
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK HYDROVAIRE VENTURIS
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK HYDROVAIRE GUAGES
LPB | LIQUID PROPANE BOILER | SPRING | [ ] CHECK AQUAVAIRE SAFETIES
LPB | LIQUID PROPANE BOILER | SPRING | [ ] RECORD ALL CUAGE READINGS
LPB | LIQUID PROPANE BOILER | SPRING | ________________WATERBATH TEMPERATURE
LPB | LIQUID PROPANE BOILER | SPRING | ________________PROPANE PRESSURE AT AQUAVAIRE
LPB | LIQUID PROPANE BOILER | SPRING | ________________HYDROVAIRE PRESSURE
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK SUPPLY VOLTAGE
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK MOTOR AMPS
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK GAS PRESSURES__________________________
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK FOR GAS LEAKS
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK H2O/GLYCOL LEVEL
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK FLAME SIGNAL
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK HYDROVAIRE VENTURIS
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK HYDROVAIRE GUAGES
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] CHECK AQUAVAIRE SAFETIES
LPB | LIQUID PROPANE BOILER | SUMMER | [ ] RECORD ALL CUAGE READINGS
LPB | LIQUID PROPANE BOILER | SUMMER | ________________WATERBATH TEMPERATURE
LPB | LIQUID PROPANE BOILER | SUMMER | ________________PROPANE PRESSURE AT AQUAVAIRE
LPB | LIQUID PROPANE BOILER | SUMMER | ________________HYDROVAIRE PRESSURE
LS | LASER SCAN | FALL | [ ] USING INFRARED SCANNER, MEASURE TEMPERATURE OF
LS | LASER SCAN | FALL | BREAKERS IN ELECTRICAL CIRCUIT PANELS. ZERO IN ON
LS | LASER SCAN | FALL | ANY BREAKERS THAT ARE CONSIDERABLY WARMER THAN THE
LS | LASER SCAN | FALL | AVERAGE IN THAT PANEL. CHECK BREAKER FOR DAMAGE OR
LS | LASER SCAN | FALL | OBVIOUS PROBLEMS. IF BREAKER IS A SERIOUS PROBLEM
LS | LASER SCAN | FALL | INVESTIGATE IF IT CAN BE TURNED OFF AND NOT CAUSE
LS | LASER SCAN | FALL | OPERATIONAL PROBLEMS FOR THE BRANCH AND TURN IT OFF.
LS | LASER SCAN | FALL | BE SURE TO MARK BREAKER AND ADVISE BRANCH MANAGER
LS | LASER SCAN | FALL | IF YOU TURN ONE OFF. OTHERWISE LEAVE BREAKER ON.
LS | LASER SCAN | FALL | CONTACT MACDONALD MILLER WITH INFORMATION ON THE
LS | LASER SCAN | FALL | BREAKER, WHAT PANEL, WHAT IT SERVES, ETC. THEY
LS | LASER SCAN | FALL | WILL NOTIFY THE BANK AND GET APPROVAL FOR AN
LS | LASER SCAN | FALL | ELECTRICIAN TO REPAIR OR REPLACE.
LS | LASER SCAN | FALL | [ ] NOTES________________________________________________
LS | LASER SCAN | FALL | __________________________________________________________
LS | LASER SCAN | FALL | _________________________________________________________
LS | LASER SCAN | WINTER | [ ] USING INFRARED SCANNER, MEASURE TEMPERATURE OF
LS | LASER SCAN | WINTER | BREAKERS IN ELECTRICAL CIRCUIT PANELS. ZERO IN ON
LS | LASER SCAN | WINTER | ANY BREAKERS THAT ARE CONSIDERABLY WARMER THAN THE
LS | LASER SCAN | WINTER | AVERAGE IN THAT PANEL. CHECK BREAKER FOR DAMAGE OR
LS | LASER SCAN | WINTER | OBVIOUS PROBLEMS. IF BREAKER IS A SERIOUS PROBLEM
LS | LASER SCAN | WINTER | INVESTIGATE IF IT CAN BE TURNED OFF AND NOT CAUSE
LS | LASER SCAN | WINTER | OPERATIONAL PROBLEMS FOR THE BRANCH AND TURN IT OFF.
LS | LASER SCAN | WINTER | BE SURE TO MARK BREAKER AND ADVISE BRANCH MANAGER
LS | LASER SCAN | WINTER | IF YOU TURN ONE OFF. OTHERWISE LEAVE BREAKER ON.
LS | LASER SCAN | WINTER | CONTACT MACDONALD MILLER WITH INFORMATION ON THE
LS | LASER SCAN | WINTER | BREAKER, WHAT PANEL, WHAT IT SERVES, ETC. THEY
LS | LASER SCAN | WINTER | WILL NOTIFY THE BANK AND GET APPROVAL FOR AN
LS | LASER SCAN | WINTER | ELECTRICIAN TO REPAIR OR REPLACE.
LS | LASER SCAN | WINTER | [ ] NOTES________________________________________________
LS | LASER SCAN | WINTER | __________________________________________________________
LS | LASER SCAN | WINTER | _________________________________________________________
LS | LASER SCAN | SPRING | [ ] USING INFRARED SCANNER, MEASURE TEMPERATURE OF
LS | LASER SCAN | SPRING | BREAKERS IN ELECTRICAL CIRCUIT PANELS. ZERO IN ON
LS | LASER SCAN | SPRING | ANY BREAKERS THAT ARE CONSIDERABLY WARMER THAN THE
LS | LASER SCAN | SPRING | AVERAGE IN THAT PANEL. CHECK BREAKER FOR DAMAGE OR
LS | LASER SCAN | SPRING | OBVIOUS PROBLEMS. IF BREAKER IS A SERIOUS PROBLEM
LS | LASER SCAN | SPRING | INVESTIGATE IF IT CAN BE TURNED OFF AND NOT CAUSE
LS | LASER SCAN | SPRING | OPERATIONAL PROBLEMS FOR THE BRANCH AND TURN IT OFF.
LS | LASER SCAN | SPRING | BE SURE TO MARK BREAKER AND ADVISE BRANCH MANAGER
LS | LASER SCAN | SPRING | IF YOU TURN ONE OFF. OTHERWISE LEAVE BREAKER ON.
LS | LASER SCAN | SPRING | CONTACT MACDONALD MILLER WITH INFORMATION ON THE
LS | LASER SCAN | SPRING | BREAKER, WHAT PANEL, WHAT IT SERVES, ETC. THEY
LS | LASER SCAN | SPRING | WILL NOTIFY THE BANK AND GET APPROVAL FOR AN
LS | LASER SCAN | SPRING | ELECTRICIAN TO REPAIR OR REPLACE.
LS | LASER SCAN | SPRING | [ ] NOTES________________________________________________
LS | LASER SCAN | SPRING | __________________________________________________________
LS | LASER SCAN | SPRING | _________________________________________________________
LS | LASER SCAN | SUMMER | [ ] USING INFRARED SCANNER, MEASURE TEMPERATURE OF
LS | LASER SCAN | SUMMER | BREAKERS IN ELECTRICAL CIRCUIT PANELS. ZERO IN ON
LS | LASER SCAN | SUMMER | ANY BREAKERS THAT ARE CONSIDERABLY WARMER THAN THE
LS | LASER SCAN | SUMMER | AVERAGE IN THAT PANEL. CHECK BREAKER FOR DAMAGE OR
LS | LASER SCAN | SUMMER | OBVIOUS PROBLEMS. IF BREAKER IS A SERIOUS PROBLEM
LS | LASER SCAN | SUMMER | INVESTIGATE IF IT CAN BE TURNED OFF AND NOT CAUSE
LS | LASER SCAN | SUMMER | OPERATIONAL PROBLEMS FOR THE BRANCH AND TURN IT OFF.
LS | LASER SCAN | SUMMER | BE SURE TO MARK BREAKER AND ADVISE BRANCH MANAGER
LS | LASER SCAN | SUMMER | IF YOU TURN ONE OFF. OTHERWISE LEAVE BREAKER ON.
LS | LASER SCAN | SUMMER | CONTACT MACDONALD MILLER WITH INFORMATION ON THE
LS | LASER SCAN | SUMMER | BREAKER, WHAT PANEL, WHAT IT SERVES, ETC. THEY
LS | LASER SCAN | SUMMER | WILL NOTIFY THE BANK AND GET APPROVAL FOR AN
LS | LASER SCAN | SUMMER | ELECTRICIAN TO REPAIR OR REPLACE.
LS | LASER SCAN | SUMMER | [ ] NOTES________________________________________________
LS | LASER SCAN | SUMMER | __________________________________________________________
LS | LASER SCAN | SUMMER | _________________________________________________________
MOZ | MO-SERIES OZONE SYSTEM | FALL | MONTHLY --
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
MOZ | MO-SERIES OZONE SYSTEM | FALL | LAST SERVICE AND OPERATING LIMITS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] DIS PRESS C/R _______________ NTE __________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] AIR PRESS C/R _______________ N/R __________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] ORP CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] ORP HI/LO ALARM S/P C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CYCLE PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OXYGEN REC PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OXYGEN FLOW METER C/R __________%, N/R _________%
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OXYGEN PRESS INDICATOR C/R __________BAR
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] VENTURI INLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] VENTURI OUTLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OXYGEN PRESS REG C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] COOLING WTR FLOW ALARM C/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | FALL | N/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] AIR PRESS C/R __________PSI
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] DIS TEMP C/R __________o F
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] RUN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OXYGEN GEN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | FALL | NORMAL OPERATION/OZONIA PARAMETERS SWITCH SETTINGS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] PSU - ON _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] PURGE - OFF _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] SETPOINT - REMOTE _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] OZ CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK FOR PROPER COOLING OF ELECTRODES
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] DELTA T _________o F ACROSS INLET WATER LINES
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK FOR WATER OR OZONE LEAKS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] INSP & CLEAN CABINET AIR INTAKE FILTER
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK COOLING FAN OPERATION
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TEST WATER AND OXYGEN PRESS SAFETY SWITCHES
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TEST IRON CONTENT C/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | FALL | N/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] AIR PRESS SHUT DOWN VALVE/BACKFLOW SWITCH
MOZ | MO-SERIES OZONE SYSTEM | FALL | C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | FALL | FOLLOW PROPER SEQUENCE:
MOZ | MO-SERIES OZONE SYSTEM | FALL | (1)TURN SYSTEM SWITCH TO PURGE THEN TURN OZONIA SWITCH OFF
MOZ | MO-SERIES OZONE SYSTEM | FALL | (2)CLOSE VLV#2 AT BACKFLOW, DISCONNECT LINE FROM VLV TO
MOZ | MO-SERIES OZONE SYSTEM | FALL | OZONIA (3)SLOWLY CLOSE OZS-1 VLV, SHOULD GET #1 ALARM AT
MOZ | MO-SERIES OZONE SYSTEM | FALL | PNL (4)RESTART, MAKE SURE VLV#1 IS OPEN, TAKE OUT OF PURGE
MOZ | MO-SERIES OZONE SYSTEM | FALL | OPEN VLV#2, MAKE SURE NO WATER IS IN VACUUM
MOZ | MO-SERIES OZONE SYSTEM | FALL | (5)RECONNECT LINE TO VLV#2
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CYCLE WATER VALVES, MANUAL AND AUTO (W/POWER OFF)
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CLEAN OR REPLACE OXYGEN GENERATOR INTAKE AIR FILTER
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK ALL GAS FILTER ELEMENTS FOR MOISTURE
MOZ | MO-SERIES OZONE SYSTEM | FALL | (SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CLEAN ORP PROBE & STRAINER BASKETS
MOZ | MO-SERIES OZONE SYSTEM | FALL | # OF STRAINERS _______
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK ORP PROBE CALIBRATION
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK ORP PROBE SET POINTS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CLEAN CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CALIBRATE CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK CONDUCTIVITY CONTROLLER SET POINT
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TEST OPERATION OF THE BLOWDOWN VALVE
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TEST OPERATION LAKOS DRAIN VALVE
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | FALL | AND SHIP FOR EVALUATION
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] *PERFORM TELOG MONITORING
MOZ | MO-SERIES OZONE SYSTEM | FALL | *IF APPLICABLE
MOZ | MO-SERIES OZONE SYSTEM | FALL | QUARTERLY ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] INSPECT/REPLACE IF NEEDED OXYGEN GEN FILTER ELEMENT
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TIGHTEN HI-VOLTAGE ELECT CONNECTIONS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] APPLY DI-ELECTRIC GREASE TO ELECTRICAL
MOZ | MO-SERIES OZONE SYSTEM | FALL | CONNECTIONS IF ARCING
MOZ | MO-SERIES OZONE SYSTEM | FALL | SEMI-ANNUAL ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK VENTURI FOR BUILDUP CLEAN IF NEEDED
MOZ | MO-SERIES OZONE SYSTEM | FALL | ANNUAL ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] TIGHTEN NUTS, SCREWS, FITTINGS AND ELECT CONNECTIONS
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] INSPECT AND TEST ANTI-BACKFLOW VALVE, C/R __________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] REPLACE FEED GAS FILTERS, # OF FILTERS __________
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] CHECK AIR PREP COMPONENTS & REG FOR PROPER OPERATION
MOZ | MO-SERIES OZONE SYSTEM | FALL | [ ] INSPECT AIR COMPRESSOR IN OXYGEN GENERATOR(S)
MOZ | MO-SERIES OZONE SYSTEM | WINTER | MONTHLY --
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
MOZ | MO-SERIES OZONE SYSTEM | WINTER | LAST SERVICE AND OPERATING LIMITS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] DIS PRESS C/R _______________ NTE __________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] AIR PRESS C/R _______________ N/R __________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] ORP CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] ORP HI/LO ALARM S/P C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CYCLE PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OXYGEN REC PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OXYGEN FLOW METER C/R __________%, N/R _________%
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OXYGEN PRESS INDICATOR C/R __________BAR
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] VENTURI INLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] VENTURI OUTLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OXYGEN PRESS REG C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] COOLING WTR FLOW ALARM C/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | WINTER | N/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] AIR PRESS C/R __________PSI
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] DIS TEMP C/R __________o F
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] RUN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OXYGEN GEN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | WINTER | NORMAL OPERATION/OZONIA PARAMETERS SWITCH SETTINGS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] PSU - ON _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] PURGE - OFF _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] SETPOINT - REMOTE _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] OZ CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK FOR PROPER COOLING OF ELECTRODES
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] DELTA T _________o F ACROSS INLET WATER LINES
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK FOR WATER OR OZONE LEAKS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] INSP & CLEAN CABINET AIR INTAKE FILTER
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK COOLING FAN OPERATION
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] TEST WATER AND OXYGEN PRESS SAFETY SWITCHES
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] TEST IRON CONTENT C/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | WINTER | N/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] AIR PRESS SHUT DOWN VALVE/BACKFLOW SWITCH
MOZ | MO-SERIES OZONE SYSTEM | WINTER | C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | WINTER | FOLLOW PROPER SEQUENCE:
MOZ | MO-SERIES OZONE SYSTEM | WINTER | (1)TURN SYSTEM SWITCH TO PURGE THEN TURN OZONIA SWITCH OFF
MOZ | MO-SERIES OZONE SYSTEM | WINTER | (2)CLOSE VLV#2 AT BACKFLOW, DISCONNECT LINE FROM VLV TO
MOZ | MO-SERIES OZONE SYSTEM | WINTER | OZONIA (3)SLOWLY CLOSE OZS-1 VLV, SHOULD GET #1 ALARM AT
MOZ | MO-SERIES OZONE SYSTEM | WINTER | PNL (4)RESTART, MAKE SURE VLV#1 IS OPEN, TAKE OUT OF PURGE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | OPEN VLV#2, MAKE SURE NO WATER IS IN VACUUM
MOZ | MO-SERIES OZONE SYSTEM | WINTER | (5)RECONNECT LINE TO VLV#2
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CYCLE WATER VALVES, MANUAL AND AUTO (W/POWER OFF)
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CLEAN OR REPLACE OXYGEN GENERATOR INTAKE AIR FILTER
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK ALL GAS FILTER ELEMENTS FOR MOISTURE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | (SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CLEAN ORP PROBE & STRAINER BASKETS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | # OF STRAINERS _______
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK ORP PROBE CALIBRATION
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK ORP PROBE SET POINTS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CLEAN CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CALIBRATE CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK CONDUCTIVITY CONTROLLER SET POINT
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] TEST OPERATION OF THE BLOWDOWN VALVE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] TEST OPERATION LAKOS DRAIN VALVE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | AND SHIP FOR EVALUATION
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] *PERFORM TELOG MONITORING
MOZ | MO-SERIES OZONE SYSTEM | WINTER | *IF APPLICABLE
MOZ | MO-SERIES OZONE SYSTEM | WINTER | QUARTERLY ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] INSPECT/REPLACE IF NEEDED OXYGEN GEN FILTER ELEMENT
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] TIGHTEN HI-VOLTAGE ELECT CONNECTIONS
MOZ | MO-SERIES OZONE SYSTEM | WINTER | [ ] APPLY DI-ELECTRIC GREASE TO ELECTRICAL
MOZ | MO-SERIES OZONE SYSTEM | WINTER | CONNECTIONS IF ARCING
MOZ | MO-SERIES OZONE SYSTEM | SPRING | MONTHLY --
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
MOZ | MO-SERIES OZONE SYSTEM | SPRING | LAST SERVICE AND OPERATING LIMITS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] DIS PRESS C/R _______________ NTE __________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] AIR PRESS C/R _______________ N/R __________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] ORP CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] ORP HI/LO ALARM S/P C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CYCLE PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OXYGEN REC PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OXYGEN FLOW METER C/R __________%, N/R _________%
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OXYGEN PRESS INDICATOR C/R __________BAR
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] VENTURI INLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] VENTURI OUTLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OXYGEN PRESS REG C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] COOLING WTR FLOW ALARM C/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | SPRING | N/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] AIR PRESS C/R __________PSI
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] DIS TEMP C/R __________o F
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] RUN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OXYGEN GEN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | SPRING | NORMAL OPERATION/OZONIA PARAMETERS SWITCH SETTINGS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] PSU - ON _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] PURGE - OFF _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] SETPOINT - REMOTE _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] OZ CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK FOR PROPER COOLING OF ELECTRODES
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] DELTA T _________o F ACROSS INLET WATER LINES
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK FOR WATER OR OZONE LEAKS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] INSP & CLEAN CABINET AIR INTAKE FILTER
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK COOLING FAN OPERATION
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] TEST WATER AND OXYGEN PRESS SAFETY SWITCHES
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] TEST IRON CONTENT C/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | SPRING | N/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] AIR PRESS SHUT DOWN VALVE/BACKFLOW SWITCH
MOZ | MO-SERIES OZONE SYSTEM | SPRING | C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SPRING | FOLLOW PROPER SEQUENCE:
MOZ | MO-SERIES OZONE SYSTEM | SPRING | (1)TURN SYSTEM SWITCH TO PURGE THEN TURN OZONIA SWITCH OFF
MOZ | MO-SERIES OZONE SYSTEM | SPRING | (2)CLOSE VLV#2 AT BACKFLOW, DISCONNECT LINE FROM VLV TO
MOZ | MO-SERIES OZONE SYSTEM | SPRING | OZONIA (3)SLOWLY CLOSE OZS-1 VLV, SHOULD GET #1 ALARM AT
MOZ | MO-SERIES OZONE SYSTEM | SPRING | PNL (4)RESTART, MAKE SURE VLV#1 IS OPEN, TAKE OUT OF PURGE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | OPEN VLV#2, MAKE SURE NO WATER IS IN VACUUM
MOZ | MO-SERIES OZONE SYSTEM | SPRING | (5)RECONNECT LINE TO VLV#2
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CYCLE WATER VALVES, MANUAL AND AUTO (W/POWER OFF)
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CLEAN OR REPLACE OXYGEN GENERATOR INTAKE AIR FILTER
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK ALL GAS FILTER ELEMENTS FOR MOISTURE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | (SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CLEAN ORP PROBE & STRAINER BASKETS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | # OF STRAINERS _______
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK ORP PROBE CALIBRATION
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK ORP PROBE SET POINTS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CLEAN CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CALIBRATE CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK CONDUCTIVITY CONTROLLER SET POINT
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] TEST OPERATION OF THE BLOWDOWN VALVE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] TEST OPERATION LAKOS DRAIN VALVE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | AND SHIP FOR EVALUATION
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] *PERFORM TELOG MONITORING
MOZ | MO-SERIES OZONE SYSTEM | SPRING | *IF APPLICABLE
MOZ | MO-SERIES OZONE SYSTEM | SPRING | QUARTERLY ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] INSPECT/REPLACE IF NEEDED OXYGEN GEN FILTER ELEMENT
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] TIGHTEN HI-VOLTAGE ELECT CONNECTIONS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] APPLY DI-ELECTRIC GREASE TO ELECTRICAL
MOZ | MO-SERIES OZONE SYSTEM | SPRING | CONNECTIONS IF ARCING
MOZ | MO-SERIES OZONE SYSTEM | SPRING | SEMI-ANNUAL ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK VENTURI FOR BUILDUP CLEAN IF NEEDED
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | MONTHLY --
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | LAST SERVICE AND OPERATING LIMITS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] DIS PRESS C/R _______________ NTE __________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] AIR PRESS C/R _______________ N/R __________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] ORP CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] ORP HI/LO ALARM S/P C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CYCLE PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OXYGEN REC PRESS C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OXYGEN FLOW METER C/R __________%, N/R _________%
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OXYGEN PRESS INDICATOR C/R __________BAR
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] VENTURI INLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] VENTURI OUTLET C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OXYGEN PRESS REG C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] COOLING WTR FLOW ALARM C/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | N/R __________GPM
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] AIR PRESS C/R __________PSI
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] DIS TEMP C/R __________o F
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] RUN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OXYGEN GEN HRS C/R __________HR
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | NORMAL OPERATION/OZONIA PARAMETERS SWITCH SETTINGS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] PSU - ON _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] PURGE - OFF _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] SETPOINT - REMOTE _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] OZ CONTROLLER C/R __________ N/R _________
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK FOR PROPER COOLING OF ELECTRODES
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] DELTA T _________o F ACROSS INLET WATER LINES
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK FOR WATER OR OZONE LEAKS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] INSP & CLEAN CABINET AIR INTAKE FILTER
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK COOLING FAN OPERATION
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] TEST WATER AND OXYGEN PRESS SAFETY SWITCHES
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] TEST IRON CONTENT C/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | N/R ____________MG/LTR
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] AIR PRESS SHUT DOWN VALVE/BACKFLOW SWITCH
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | C/R __________PSI, N/R _________PSI
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | FOLLOW PROPER SEQUENCE:
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | (1)TURN SYSTEM SWITCH TO PURGE THEN TURN OZONIA SWITCH OFF
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | (2)CLOSE VLV#2 AT BACKFLOW, DISCONNECT LINE FROM VLV TO
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | OZONIA (3)SLOWLY CLOSE OZS-1 VLV, SHOULD GET #1 ALARM AT
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | PNL (4)RESTART, MAKE SURE VLV#1 IS OPEN, TAKE OUT OF PURGE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | OPEN VLV#2, MAKE SURE NO WATER IS IN VACUUM
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | (5)RECONNECT LINE TO VLV#2
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CYCLE WATER VALVES, MANUAL AND AUTO (W/POWER OFF)
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CLEAN OR REPLACE OXYGEN GENERATOR INTAKE AIR FILTER
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK ALL GAS FILTER ELEMENTS FOR MOISTURE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | (SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CLEAN ORP PROBE & STRAINER BASKETS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | # OF STRAINERS _______
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK ORP PROBE CALIBRATION
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK ORP PROBE SET POINTS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CLEAN CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CALIBRATE CONDUCTIVITY PROBE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK CONDUCTIVITY CONTROLLER SET POINT
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] TEST OPERATION OF THE BLOWDOWN VALVE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] TEST OPERATION LAKOS DRAIN VALVE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | AND SHIP FOR EVALUATION
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] *PERFORM TELOG MONITORING
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | *IF APPLICABLE
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | QUARTERLY ADDITIONS TO CHECKLISTS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] INSPECT/REPLACE IF NEEDED OXYGEN GEN FILTER ELEMENT
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] TIGHTEN HI-VOLTAGE ELECT CONNECTIONS
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | [ ] APPLY DI-ELECTRIC GREASE TO ELECTRICAL
MOZ | MO-SERIES OZONE SYSTEM | SUMMER | CONNECTIONS IF ARCING
MP | MICRO PROCESSOR | FALL | [ ] CHECK VOLTAGE____________________
MP | MICRO PROCESSOR | FALL | [ ] CHECK OPERATION
MP | MICRO PROCESSOR | FALL | [ ] SCAN SPACE TEMPERATURE
MP | MICRO PROCESSOR | FALL | [ ] CHECK VENTILATION FAN OPERATION
MP | MICRO PROCESSOR | WINTER | [ ] CHECK VOLTAGE____________________-
MP | MICRO PROCESSOR | WINTER | [ ] CHECK OPERATION
MP | MICRO PROCESSOR | WINTER | [ ] SCAN SPACE TEMPERATURE
MP | MICRO PROCESSOR | WINTER | [ ] CHECK VENTILATION FAN OPERATION
MP | MICRO PROCESSOR | SPRING | [ ] CHECK VOLTAGE_____________________
MP | MICRO PROCESSOR | SPRING | [ ] CHECK OPERATION
MP | MICRO PROCESSOR | SPRING | [ ] SCAN SPACE TEMPERATURE
MP | MICRO PROCESSOR | SPRING | [ ] CHECK VENTILATION FAN OPERATION
MP | MICRO PROCESSOR | SUMMER | [ ] CHECK VOLTAGE__________________
MP | MICRO PROCESSOR | SUMMER | [ ] CHECK OPERATION
MP | MICRO PROCESSOR | SUMMER | [ ] SCAN SPACE TEMPERATURE
MP | MICRO PROCESSOR | SUMMER | [ ] CHECK VENTILATION FAN OPERATION
MTR | MOTOR | FALL | [ ] CHECK OPERATION
MTR | MOTOR | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MTR | MOTOR | FALL | [ ] CHECK AMPS_______________________
MTR | MOTOR | FALL | [ ] CHECK VOLTAGE____________________
MTR | MOTOR | FALL | [ ] INSPECT MOTOR COUPLER
MTR | MOTOR | FALL | [ ] INSPECT PULLEY
MTR | MOTOR | FALL | [ ] CHECK BELT
MTR | MOTOR | WINTER | [ ] CHECK OPERATION
MTR | MOTOR | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MTR | MOTOR | WINTER | [ ] CHECK AMPS___________________
MTR | MOTOR | WINTER | [ ] CHECK VOLTAGE________________
MTR | MOTOR | WINTER | [ ] INSPECT MOTOR COUPLER
MTR | MOTOR | WINTER | [ ] INSPECT PULLEY
MTR | MOTOR | WINTER | [ ] CHECK BELT
MTR | MOTOR | WINTER | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
MTR | MOTOR | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
MTR | MOTOR | WINTER | [ ] CHECK CONTACTOR POINTS
MTR | MOTOR | WINTER | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
MTR | MOTOR | WINTER | [ ] MEG OHM MOTOR (10 HP OR LARGER)
MTR | MOTOR | SPRING | [ ] CHECK OPERATION
MTR | MOTOR | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MTR | MOTOR | SPRING | [ ] CHECK AMPS__________________________
MTR | MOTOR | SPRING | [ ] CHECK VOLTAGE_______________________
MTR | MOTOR | SPRING | [ ] INSPECT MOTOR COUPLER
MTR | MOTOR | SPRING | [ ] INSPECT PULLEY
MTR | MOTOR | SPRING | [ ] CHECK BELT
MTR | MOTOR | SPRING | [ ] LUBRICATION MOTOR BEARINGS (PER MFG SPECS)
MTR | MOTOR | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
MTR | MOTOR | SPRING | [ ] CHECK CONTACTOR POINTS
MTR | MOTOR | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
MTR | MOTOR | SUMMER | [ ] CHECK OPERATION
MTR | MOTOR | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MTR | MOTOR | SUMMER | [ ] CHECK AMPS_________________________
MTR | MOTOR | SUMMER | [ ] CHECK VOLTAGE______________________
MTR | MOTOR | SUMMER | [ ] INSPECT MOTOR COUPLER
MTR | MOTOR | SUMMER | [ ] INSPECT PULLEY
MTR | MOTOR | SUMMER | [ ] CHECK BELT
MTR | MOTOR | SUMMER | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
MTR | MOTOR | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
MTR | MOTOR | SUMMER | [ ] CHECK CONTACTOR POINTS
MTR | MOTOR | SUMMER | [ ] MEG OHM MOTOR (10HP OR LARGER)
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK BLOWER OPERATION
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK DAMPER OPERATION
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK BLOWER BELTS
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK BELT ALIGNMENT
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK PULLEY WEAR
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK BURNER OPERATION
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK OPERATIONAL SEQUENCE
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK COMBUSTION BLOWER WHEEL, CLEAN IF REQUIRED
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK DAMPER ACTUATOR INTERLOCKS
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK TIME DELAY
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK AIR PROVING SWITCH
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK TEMPERATURE CONTROL
MU | MAKE UP AIR UNIT | FALL | [ ] CLEAN BURNER ORIFICES
MU | MAKE UP AIR UNIT | FALL | [ ] INSPECT IGNITOR AND CHECK GAP
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK GAS MANIFOLD PRESSURE_______________"WC
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK TEMPERATURE RISE__________________DEG F
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK MAIN LINE GAS PRESSURE_____________"WC
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK PILOT GAS VALVE
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK MODULATING GAS VALVE
MU | MAKE UP AIR UNIT | FALL | [ ] MEG OHM MOTOR (10HP OR LARGER)
MU | MAKE UP AIR UNIT | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
MU | MAKE UP AIR UNIT | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK CONTACTOR POINTS
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK VOLTAGE L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | FALL | [ ] CHECK AMP DRAW L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK BLOWER OPERATION
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK DAMPER OPERATION
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK BLOWER BELTS
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK BELT ALIGNMENT
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK PULLEY WEAR
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK BURNER OPERATION
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK OPERATIONAL SEQUENCE
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK VOLTAGE L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | WINTER | [ ] CHECK AMP DRAW L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | SPRING | [ ] LUBRICATE BLOWER BEARING (PER MFG SPECS)
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK BLOWER OPERATION
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK DAMPER OPERATION
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK BLOWER BELTS
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK BELT ALIGNMENT
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK PULLEY WEAR
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK BURNER OPERATION
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK OPERATIONAL SEQUENCE
MU | MAKE UP AIR UNIT | SPRING | ON ALL THREE PHASE MOTORS
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK AMPS L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | SPRING | [ ] CHECK VOLTAGE L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK BLOWER OPERATION
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK BLOWER BELTS
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK BELT ALIGNMENT
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK PULLEY WEAR
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK BURNER OPERATION
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK OPERATIONAL SEQUENCE
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK VOLTAGE L1_____L2_____L3_____
MU | MAKE UP AIR UNIT | SUMMER | [ ] CHECK AMP DRAW L1_____L2_____L3_____
MZ | MULTIZONE UNIT | FALL | [ ] CHECK OPERATION OF ALL DAMPER MOTORS AND LINKAGES
MZ | MULTIZONE UNIT | FALL | [ ] CHECK BELTS AND PULLEYS
MZ | MULTIZONE UNIT | FALL | [ ] LUBRICATE MOTOR AND BLOWER BEARINGS (PER MFG SPECS)
MZ | MULTIZONE UNIT | FALL | [ ] CHECK AND CLEAN BLOWER WHEELS
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | HEATING OPERATION - ELECTRIC HEAT
MZ | MULTIZONE UNIT | FALL | [ ] CHECK AMP DRAW ON ELEMENTS______________________
MZ | MULTIZONE UNIT | FALL | [ ] CHECK ALL SAFETY DEVICES
MZ | MULTIZONE UNIT | FALL | [ ] CHECK TEMPERATURE RISE___________________DEG.F.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | GAS HEAT
MZ | MULTIZONE UNIT | FALL | [ ] CHECK MAIN LINE GAS PRESSURE_______________" W.C.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK MANIFOLD GAS PRESSURE________________" W.C.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK HEAT EXCHANGER FOR CRACKS
MZ | MULTIZONE UNIT | FALL | [ ] CHECK FLAME SIZE AND COLOR
MZ | MULTIZONE UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | FALL | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
MZ | MULTIZONE UNIT | FALL | [ ] CHECK TEMPERATURE RISE____________________DEG.F.
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | HOT WATER HEAT
MZ | MULTIZONE UNIT | FALL | [ ] CHECK OPERATION OF THREE-WAY WATER VALVE
MZ | MULTIZONE UNIT | FALL | [ ] CHECK WATER TEMPERATURE___________________DEG.F.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK TEMPERATURE RISE____________________DEG.F.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | FALL | COOLING OPERATION
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | ECONOMIZER
MZ | MULTIZONE UNIT | FALL | [ ] CHECK ECONOMIZER OPERATIONS
MZ | MULTIZONE UNIT | FALL | [ ] CHECK RELIEF DAMPERS
MZ | MULTIZONE UNIT | FALL | [ ] CHECK CONTROL SET-POINTS
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | MECHANICAL COOLING
MZ | MULTIZONE UNIT | FALL
MZ | MULTIZONE UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | FALL | [ ] CHECK INDOOR COIL TEMPERATURE DROP__________DEG.F.
MZ | MULTIZONE UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
MZ | MULTIZONE UNIT | FALL | [ ] CHECK CRANKCASE HEATER
MZ | MULTIZONE UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
MZ | MULTIZONE UNIT | FALL | [ ] CHECK COMPRESSOR OIL LEVEL
MZ | MULTIZONE UNIT | FALL | [ ] ADD PAN TABLETS
MZ | MULTIZONE UNIT | FALL | [ ] CHECK CONDENSATE PAN AND TRAP
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK OPERATION OF ALL DAMPER MOTORS AND LINKAGES
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK BELTS AND PULLEYS
MZ | MULTIZONE UNIT | WINTER
MZ | MULTIZONE UNIT | WINTER | HEATING OPERATION
MZ | MULTIZONE UNIT | WINTER | ELECTRIC HEAT
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK ALL SAFETY DEVICES
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | WINTER
MZ | MULTIZONE UNIT | WINTER | GAS HEAT
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK FLAME SIZE AND COLOR
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
MZ | MULTIZONE UNIT | WINTER | HOT WATER HEAT
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK OPERATION OF THREE-WAY WATER VALVE
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK WATER TEMPERATURE_____________DEG.F.
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | WINTER
MZ | MULTIZONE UNIT | WINTER | COOLING OPERATION
MZ | MULTIZONE UNIT | WINTER | ECONOMIZER
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK ECONOMIZER OPERATION
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK RELIEF DAMPERS
MZ | MULTIZONE UNIT | WINTER | [ ] CHECK CONTROL SET-POINTS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK OPERATION OF ALL DAMPER MOTORS AND LINKAGES
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK BELTS AND PULLEYS
MZ | MULTIZONE UNIT | SPRING | [ ] LUBRICATE MOTOR AND BLOWER BEARINGS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK AND CLEAN BLOWER WHEELS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS AND COMPONENTS
MZ | MULTIZONE UNIT | SPRING
MZ | MULTIZONE UNIT | SPRING | HEATING OPERATION
MZ | MULTIZONE UNIT | SPRING | ELECTRIC HEAT
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK ALL SAFETY DEVICES
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
MZ | MULTIZONE UNIT | SPRING
MZ | MULTIZONE UNIT | SPRING | GAS HEAT
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK FLAME SIZE AND COLOR
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
MZ | MULTIZONE UNIT | SPRING
MZ | MULTIZONE UNIT | SPRING | HOT WATER HEAT
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK OPERATION OF THREE-WAY WATER VALVE
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK WATER TEMPERATURE__________________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SPRING
MZ | MULTIZONE UNIT | SPRING | COOLING OPERATION
MZ | MULTIZONE UNIT | SPRING | ECONOMIZER
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK ECONOMIZER OPERATION
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK RELIEF DAMPERS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK CONTROL SETPOINTS
MZ | MULTIZONE UNIT | SPRING | MECHANICAL COOLING
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK INDOOR COIL TEMPERATURE DROP__________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK COMPRESSOR OIL LEVEL
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE_________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SUPERHEAT AT COMPRESSOR________________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SUBCOOLING____________________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK EXPANSION VALVE AND BULB
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK CAPICITY CONTROLS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK OPERATION PRESSURES HP_________LP_________
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK SAFETIES
MZ | MULTIZONE UNIT | SPRING | [ ] MEGG/OHM MOTORS AND COMPRESSORS 10 HP OR LARGER
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK OUTDOOR FAN BLADES AND SUPPORTS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK COMPRESSOR DISCHARGE LINE
MZ | MULTIZONE UNIT | SPRING | TEMPERATURE__________DEG.F.
MZ | MULTIZONE UNIT | SPRING | [ ] ADD PAN TABLETS
MZ | MULTIZONE UNIT | SPRING | [ ] CHECK CONDENSATE PAN AND TRAP
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK OPERATION OF ALL DAMPER MOTORS AND LINKAGES
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK BELTS AND PULLEYS
MZ | MULTIZONE UNIT | SUMMER
MZ | MULTIZONE UNIT | SUMMER | HEATING OPERATION
MZ | MULTIZONE UNIT | SUMMER | ELECTRIC HEAT
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK ALL SAFETY DEVICES
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SUMMER
MZ | MULTIZONE UNIT | SUMMER | GAS HEAT
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK FLAME SIZE AND COLOR
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK ALL CONTROLS AND SAFETY DEVICES
MZ | MULTIZONE UNIT | SUMMER
MZ | MULTIZONE UNIT | SUMMER | HOT WATER HEAT
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK OPERATION OF THREE-WAY WATER VALVE
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK WATER TEMPERATURE
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SUMMER | COOLING OPERATION
MZ | MULTIZONE UNIT | SUMMER | ECONOMIZER
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK ECONOMIZER OPERATION
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK RELIEF DAMPERS
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK CONTROL SET-POINTS
MZ | MULTIZONE UNIT | SUMMER
MZ | MULTIZONE UNIT | SUMMER | MECHANICAL COOLING
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK INDOOR COIL TEMPERATURE DROP_____________DEG.F.
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK COMPRESSOR OIL LEVEL
MZ | MULTIZONE UNIT | SUMMER | [ ] ADD PAN TABLETS
MZ | MULTIZONE UNIT | SUMMER | [ ] CHECK CONDENSATE PAN AND TRAP
OF | OIL FURNACE | FALL | [ ] CHECK AND CLEAN BLOWER WHEELS
OF | OIL FURNACE | FALL | [ ] LUBRICATE MOTORS AND BEARINGS (PER MFG SPECS)
OF | OIL FURNACE | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
OF | OIL FURNACE | FALL | [ ] CHECK TEMPERATURE RISE__________________DEG.F.
OF | OIL FURNACE | FALL | [ ] CHECK OIL TANK LEVEL________________________% FULL
OF | OIL FURNACE | FALL | [ ] CHECK OIL PUMP PRESSURE_________________________PSIG
OF | OIL FURNACE | FALL | [ ] CHECK FUEL LINE FILTER
OF | OIL FURNACE | FALL | [ ] CHECK OIL PUMP STRAINER
OF | OIL FURNACE | FALL | [ ] CLEAN GUN ASSEMBLY
OF | OIL FURNACE | FALL | [ ] CLEAN ELECTRODES AND CHECK GAP_____________"
OF | OIL FURNACE | FALL | [ ] CHECK CO2_______________%
OF | OIL FURNACE | FALL | [ ] INSPECT COMBUSTION CHAMBER FOR CRACKS
OF | OIL FURNACE | FALL | [ ] INSPECT HEAT EXCHANGER FOR SOOT
OF | OIL FURNACE | WINTER | [ ] CHECK AND CLEAN BLOWER WHEELS
OF | OIL FURNACE | WINTER | [ ] CHECK TEMPERATURE RISE_________________DEG.F.
OF | OIL FURNACE | WINTER | [ ] CHECK OIL TANK LEVEL_____________________%FULL
OF | OIL FURNACE | WINTER | [ ] CEHCK OIL PUMP PRESSURE____________________PSIG
OF | OIL FURNACE | WINTER | [ ] CHECK FUEL LINE FILTER
OF | OIL FURNACE | WINTER | [ ] CHECK OIL PUMP STRAINER
OF | OIL FURNACE | WINTER | [ ] CLEAN GUN ASSEMBLY
OF | OIL FURNACE | WINTER | [ ] CLEAN ELECTRODES AND CHECK GAP_____________"
OF | OIL FURNACE | SPRING | [ ] CHECK AND CLEAN BLOWER WHEELS
OF | OIL FURNACE | SPRING | [ ] CHECK TEMPERATURE RISE______________DEG.F.
OF | OIL FURNACE | SPRING | [ ] CHECK OIL TANK LEVEL____________________%FULL
OF | OIL FURNACE | SPRING | [ ] CHECK OIL PUMP PRESSURE____________________PSIG
OF | OIL FURNACE | SPRING | [ ] CHECK FUEL LINE FILTER
OF | OIL FURNACE | SPRING | [ ] CHECK OIL PUMP STRAINER
OF | OIL FURNACE | SPRING | [ ] CLEAN ELECTRODES AND CHECK GAP______________"
OF | OIL FURNACE | SUMMER | [ ] CLEAN AND CHECK BLOWER WHEELS
OF | OIL FURNACE | SUMMER | [ ] CHECK TEMPERATURE RISE________________DEG.F.
OF | OIL FURNACE | SUMMER | [ ] CHECK OIL TANK LEVEL________________%FULL
OF | OIL FURNACE | SUMMER | [ ] CHECK OIL PUMP PRESSURE______________PSIG
OF | OIL FURNACE | SUMMER | [ ] CHECK FUEL LINE FILTER
OF | OIL FURNACE | SUMMER | [ ] CHECK OIL PUMP STRAINER
OF | OIL FURNACE | SUMMER | [ ] CLEAN ELECTRODES AND CHECK GAP______________"
OFN | OSCILLATING FAN | FALL | [ ] CHECK OPERATION
OFN | OSCILLATING FAN | FALL | [ ] LUBE AS NEEDED
OFN | OSCILLATING FAN | WINTER | [ ] CHECK OPERATION
OFN | OSCILLATING FAN | WINTER | [ ] LUBE AS NECESSARY
OFN | OSCILLATING FAN | SPRING | [ ] CHECK OPERATION
OFN | OSCILLATING FAN | SPRING | [ ] LUBE AS NECESSARY
OFN | OSCILLATING FAN | SUMMER | [ ] CHECK OPERATION
OFN | OSCILLATING FAN | SUMMER | [ ] LUBE AS NECESSARY
OP | OPERATIONAL CK ONLY | FALL | [ ] TURN ON DISCONNECT
OP | OPERATIONAL CK ONLY | FALL | [ ] TURN ON THERMOSTAT
OP | OPERATIONAL CK ONLY | FALL | [ ] UNIT RUNS OK YES________NO________
OP | OPERATIONAL CK ONLY | FALL | [ ] NOTIFY DENNIS SMITH OF ANY PROBLEMS
OP | OPERATIONAL CK ONLY | FALL | [ ] DO NOT DO A FULL MAINTENANCE
OP | OPERATIONAL CK ONLY | FALL | [ ] DO NOT DO ANY REPAIRS
OP | OPERATIONAL CK ONLY | WINTER | [ ] TURN ON DISCONNECT
OP | OPERATIONAL CK ONLY | WINTER | [ ] TURN ON THERMOSTAT
OP | OPERATIONAL CK ONLY | WINTER | [ ] UNIT RUNS OK YES______NO______
OP | OPERATIONAL CK ONLY | WINTER | [ ] NOTIFY DENNIS SMITH OF ANY PROBLEMS
OP | OPERATIONAL CK ONLY | WINTER | [ ] DO NOT DO A FULL MAINTENANCE
OP | OPERATIONAL CK ONLY | WINTER | [ ] DO NOT DO ANY REPAIRS
OP | OPERATIONAL CK ONLY | SPRING | [ ] TURN ON DISCONNECT
OP | OPERATIONAL CK ONLY | SPRING | [ ] TURN ON THERMOSTAT
OP | OPERATIONAL CK ONLY | SPRING | [ ] UNIT RUNS OK YES______NO______
OP | OPERATIONAL CK ONLY | SPRING | [ ] NOTIFY DENNIS SMITH OF ANY PROBLEMS
OP | OPERATIONAL CK ONLY | SPRING | [ ] DO NOT DO A FULL MAINTENANCE
OP | OPERATIONAL CK ONLY | SPRING | [ ] DO NOT DO ANY REPAIRS
OP | OPERATIONAL CK ONLY | SUMMER | [ ] TURN ON DISCONNECT
OP | OPERATIONAL CK ONLY | SUMMER | [ ] TURN ON THERMOSTAT
OP | OPERATIONAL CK ONLY | SUMMER | [ ] UNIT RUNS OK YES______NO______
OP | OPERATIONAL CK ONLY | SUMMER | [ ] NOTIFY DENNIS SMITH OF ANY PROBLEMS
OP | OPERATIONAL CK ONLY | SUMMER | [ ] DO NOT DO A FULL MAINTENANCE
OP | OPERATIONAL CK ONLY | SUMMER | [ ] DO NOT DO ANY REPAIRS
OV | CONVECTION OVEN | FALL | QUARTERLY
OV | CONVECTION OVEN | FALL | [ ] CHECK THAT SAFETY SHUT OFF VALVE OPERATES PROPERLY
OV | CONVECTION OVEN | FALL | PER MANUFACTURERS LEAK TEST PROCEDURES
OV | CONVECTION OVEN | FALL | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | FALL | AS NECESSARY
OV | CONVECTION OVEN | FALL | [ ] CHECK AND TEST SAFETY CONTROLS, FOLLOWING MANUFACTURE
OV | CONVECTION OVEN | FALL | SAFETY CONTROL TEST
OV | CONVECTION OVEN | FALL | [ ] CHECK COMBUSTION SAFEGUARD BY SIMULATING FLAME FAILUR
OV | CONVECTION OVEN | FALL | [ ] LUBRICATE BEARINGS ON BLOWERS
OV | CONVECTION OVEN | FALL
OV | CONVECTION OVEN | FALL | ANNUALLY
OV | CONVECTION OVEN | FALL | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | FALL | AS NECESSARY; REPLACE THEM AS NEEDED ON T&M BASIS
OV | CONVECTION OVEN | FALL | [ ] VERIFY CORRECT SETTING OF TIME DELAY RELAYS FOR THE
OV | CONVECTION OVEN | FALL | PURGE TIMERS
OV | CONVECTION OVEN | FALL | [ ] VERIFY OPERATION OF ALL AIR FLOW SWITCHES BY
OV | CONVECTION OVEN | FALL | SIMULATING LOSS OF AIR FLOW
OV | CONVECTION OVEN | FALL | [ ] VERIFY FAN INTERLOCKS OPERATE PROPERLY
OV | CONVECTION OVEN | FALL | [ ] VERIFY THAT PURGE TIMER OPERATES PROPERLY
OV | CONVECTION OVEN | FALL | [ ] VERIFY THAT CONVEYOR (AS APPLICABLE) WILL NOT
OV | CONVECTION OVEN | FALL | OPERATE WHEN VENTILATION SYSTEM IS INOPERATIVE
OV | CONVECTION OVEN | FALL | [ ] VERIFY PROPER OPERATION OF HIGH AND LOW GAS PRESSURE
OV | CONVECTION OVEN | FALL | SWITCH
OV | CONVECTION OVEN | FALL | [ ] CALIBRATE AND TEST OVEN TEMPERATURE CONTROLLER
OV | CONVECTION OVEN | FALL | [ ] OPERATE THE OVEN AT ABOVE NORMAL TEMPERATURE TO
OV | CONVECTION OVEN | FALL | VERIFY THAT THE TEMPERATURE LIMIT IS SET AND
OV | CONVECTION OVEN | FALL | OPERATING PROPERLY
OV | CONVECTION OVEN | FALL | [ ] MEASURE EXHAUST DUCT AIR VELOCITY AND CALCULATE
OV | CONVECTION OVEN | FALL | ACTUAL EXHAUST AIR QUANTITY
OV | CONVECTION OVEN | WINTER | QUARTERLY
OV | CONVECTION OVEN | WINTER | [ ] CHECK THAT SAFETY SHUT OFF VALVE OPERATES PROPERLY
OV | CONVECTION OVEN | WINTER | PER MANUFACTURERS LEAK TEST PROCEDURES
OV | CONVECTION OVEN | WINTER | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | WINTER | AS NECESSARY
OV | CONVECTION OVEN | WINTER | [ ] CHECK AND TEST SAFETY CONTROLS, FOLLOWING MANUFACTURE
OV | CONVECTION OVEN | WINTER | SAFETY CONTROL TEST
OV | CONVECTION OVEN | WINTER | [ ] CHECK COMBUSTION SAFEGUARD BY SIMULATING FLAME FAILUR
OV | CONVECTION OVEN | WINTER | [ ] LUBRICATE BEARINGS ON BLOWERS
OV | CONVECTION OVEN | WINTER
OV | CONVECTION OVEN | WINTER | ANNUALLY
OV | CONVECTION OVEN | WINTER | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | WINTER | AS NECESSARY; REPLACE THEM AS NEEDED ON T&M BASIS
OV | CONVECTION OVEN | WINTER | [ ] VERIFY CORRECT SETTING OF TIME DELAY RELAYS FOR THE
OV | CONVECTION OVEN | WINTER | PURGE TIMERS
OV | CONVECTION OVEN | WINTER | [ ] VERIFY OPERATION OF ALL AIR FLOW SWITCHES BY
OV | CONVECTION OVEN | WINTER | SIMULATING LOSS OF AIR FLOW
OV | CONVECTION OVEN | WINTER | [ ] VERIFY FAN INTERLOCKS OPERATE PROPERLY
OV | CONVECTION OVEN | WINTER | [ ] VERIFY THAT PURGE TIMER OPERATES PROPERLY
OV | CONVECTION OVEN | WINTER | [ ] VERIFY THAT CONVEYOR (AS APPLICABLE) WILL NOT
OV | CONVECTION OVEN | WINTER | OPERATE WHEN VENTILATION SYSTEM IS INOPERATIVE
OV | CONVECTION OVEN | WINTER | [ ] VERIFY PROPER OPERATION OF HIGH AND LOW GAS PRESSURE
OV | CONVECTION OVEN | WINTER | SWITCH
OV | CONVECTION OVEN | WINTER | [ ] CALIBRATE AND TEST OVEN TEMPERATURE CONTROLLER
OV | CONVECTION OVEN | WINTER | [ ] OPERATE THE OVEN AT ABOVE NORMAL TEMPERATURE TO
OV | CONVECTION OVEN | WINTER | VERIFY THAT THE TEMPERATURE LIMIT IS SET AND
OV | CONVECTION OVEN | WINTER | OPERATING PROPERLY
OV | CONVECTION OVEN | WINTER | [ ] MEASURE EXHAUST DUCT AIR VELOCITY AND CALCULATE
OV | CONVECTION OVEN | WINTER | ACTUAL EXHAUST AIR QUANTITY
OV | CONVECTION OVEN | SPRING | QUARTERLY
OV | CONVECTION OVEN | SPRING | [ ] CHECK THAT SAFETY SHUT OFF VALVE OPERATES PROPERLY
OV | CONVECTION OVEN | SPRING | PER MANUFACTURERS LEAK TEST PROCEDURES
OV | CONVECTION OVEN | SPRING | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | SPRING | AS NECESSARY
OV | CONVECTION OVEN | SPRING | [ ] CHECK AND TEST SAFETY CONTROLS, FOLLOWING MANUFACTURE
OV | CONVECTION OVEN | SPRING | SAFETY CONTROL TEST
OV | CONVECTION OVEN | SPRING | [ ] CHECK COMBUSTION SAFEGUARD BY SIMULATING FLAME FAILUR
OV | CONVECTION OVEN | SPRING | [ ] LUBRICATE BEARINGS ON BLOWERS
OV | CONVECTION OVEN | SPRING
OV | CONVECTION OVEN | SPRING | ANNUALLY
OV | CONVECTION OVEN | SPRING | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | SPRING | AS NECESSARY; REPLACE THEM AS NEEDED ON T&M BASIS
OV | CONVECTION OVEN | SPRING | [ ] VERIFY CORRECT SETTING OF TIME DELAY RELAYS FOR THE
OV | CONVECTION OVEN | SPRING | PURGE TIMERS
OV | CONVECTION OVEN | SPRING | [ ] VERIFY OPERATION OF ALL AIR FLOW SWITCHES BY
OV | CONVECTION OVEN | SPRING | SIMULATING LOSS OF AIR FLOW
OV | CONVECTION OVEN | SPRING | [ ] VERIFY FAN INTERLOCKS OPERATE PROPERLY
OV | CONVECTION OVEN | SPRING | [ ] VERIFY THAT PURGE TIMER OPERATES PROPERLY
OV | CONVECTION OVEN | SPRING | [ ] VERIFY THAT CONVEYOR (AS APPLICABLE) WILL NOT
OV | CONVECTION OVEN | SPRING | OPERATE WHEN VENTILATION SYSTEM IS INOPERATIVE
OV | CONVECTION OVEN | SPRING | [ ] VERIFY PROPER OPERATION OF HIGH AND LOW GAS PRESSURE
OV | CONVECTION OVEN | SPRING | SWITCH
OV | CONVECTION OVEN | SPRING | [ ] CALIBRATE AND TEST OVEN TEMPERATURE CONTROLLER
OV | CONVECTION OVEN | SPRING | [ ] OPERATE THE OVEN AT ABOVE NORMAL TEMPERATURE TO
OV | CONVECTION OVEN | SPRING | VERIFY THAT THE TEMPERATURE LIMIT IS SET AND
OV | CONVECTION OVEN | SPRING | OPERATING PROPERLY
OV | CONVECTION OVEN | SPRING | [ ] MEASURE EXHAUST DUCT AIR VELOCITY AND CALCULATE
OV | CONVECTION OVEN | SPRING | ACTUAL EXHAUST AIR QUANTITY
OV | CONVECTION OVEN | SUMMER | QUARTERLY
OV | CONVECTION OVEN | SUMMER | [ ] CHECK THAT SAFETY SHUT OFF VALVE OPERATES PROPERLY
OV | CONVECTION OVEN | SUMMER | PER MANUFACTURERS LEAK TEST PROCEDURES
OV | CONVECTION OVEN | SUMMER | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | SUMMER | AS NECESSARY
OV | CONVECTION OVEN | SUMMER | [ ] CHECK AND TEST SAFETY CONTROLS, FOLLOWING MANUFACTURE
OV | CONVECTION OVEN | SUMMER | SAFETY CONTROL TEST
OV | CONVECTION OVEN | SUMMER | [ ] CHECK COMBUSTION SAFEGUARD BY SIMULATING FLAME FAILUR
OV | CONVECTION OVEN | SUMMER | [ ] LUBRICATE BEARINGS ON BLOWERS
OV | CONVECTION OVEN | SUMMER
OV | CONVECTION OVEN | SUMMER | ANNUALLY
OV | CONVECTION OVEN | SUMMER | [ ] INSPECT DRIVE BELTS, ALIGN DRIVES AND TIGHTEN BELTS
OV | CONVECTION OVEN | SUMMER | AS NECESSARY; REPLACE THEM AS NEEDED ON T&M BASIS
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY CORRECT SETTING OF TIME DELAY RELAYS FOR THE
OV | CONVECTION OVEN | SUMMER | PURGE TIMERS
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY OPERATION OF ALL AIR FLOW SWITCHES BY
OV | CONVECTION OVEN | SUMMER | SIMULATING LOSS OF AIR FLOW
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY FAN INTERLOCKS OPERATE PROPERLY
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY THAT PURGE TIMER OPERATES PROPERLY
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY THAT CONVEYOR (AS APPLICABLE) WILL NOT
OV | CONVECTION OVEN | SUMMER | OPERATE WHEN VENTILATION SYSTEM IS INOPERATIVE
OV | CONVECTION OVEN | SUMMER | [ ] VERIFY PROPER OPERATION OF HIGH AND LOW GAS PRESSURE
OV | CONVECTION OVEN | SUMMER | SWITCH
OV | CONVECTION OVEN | SUMMER | [ ] CALIBRATE AND TEST OVEN TEMPERATURE CONTROLLER
OV | CONVECTION OVEN | SUMMER | [ ] OPERATE THE OVEN AT ABOVE NORMAL TEMPERATURE TO
OV | CONVECTION OVEN | SUMMER | VERIFY THAT THE TEMPERATURE LIMIT IS SET AND
OV | CONVECTION OVEN | SUMMER | OPERATING PROPERLY
OV | CONVECTION OVEN | SUMMER | [ ] MEASURE EXHAUST DUCT AIR VELOCITY AND CALCULATE
OV | CONVECTION OVEN | SUMMER | ACTUAL EXHAUST AIR QUANTITY
PLB | PLUMBING FIXTURES | FALL | [ ] INSPECT FOR WATER LEAKS
PLB | PLUMBING FIXTURES | FALL | [ ] CHECK DRAINS
PLB | PLUMBING FIXTURES | FALL | [ ] CHECK FLUSHOMETERS
PLB | PLUMBING FIXTURES | FALL | [ ] CHECK FIXTURE OPERATION
PLB | PLUMBING FIXTURES | WINTER | [ ] INSPECT FOR WATER LEAKS
PLB | PLUMBING FIXTURES | WINTER | [ ] CHECK DRAINS
PLB | PLUMBING FIXTURES | WINTER | [ ] CHECK FLUSHOMETERS
PLB | PLUMBING FIXTURES | WINTER | [ ] CHECK FIXTURE OPERATION
PLB | PLUMBING FIXTURES | SPRING | [ ] INSPECT FOR WATER LEAKS
PLB | PLUMBING FIXTURES | SPRING | [ ] CHECK DRAINS
PLB | PLUMBING FIXTURES | SPRING | [ ] CHECK FLUSHOMETERS
PLB | PLUMBING FIXTURES | SPRING | [ ] CHECK FIXTURE OPERATION
PLB | PLUMBING FIXTURES | SUMMER | [ ] INSPECT FOR WATER LEAKS
PLB | PLUMBING FIXTURES | SUMMER | [ ] CHECK DRAINS
PLB | PLUMBING FIXTURES | SUMMER | [ ] CHECK FLUSHOMETERS
PLB | PLUMBING FIXTURES | SUMMER | [ ] CHECK FIXTURE OPERATION
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK SUPPLY VOLTAGE______________________
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK MOTOR AMPS__________________________
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK PRESSURES: DISCHARGE_______________
PMP | MISCELLANEOUS PUMP | FALL | SUCTION_______________
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK FOR SEAL LEAKS
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK MOTOR AND BEARING OIL LEVEL
PMP | MISCELLANEOUS PUMP | FALL | [ ] ALTERNATE LEAD / LAG PUMP
PMP | MISCELLANEOUS PUMP | FALL | [ ] CHECK AUTOMATIC STAND-BY CHANGE OVER
PMP | MISCELLANEOUS PUMP | FALL | [ ] LUBRICATE BEARING ASSEMBLY
PMP | MISCELLANEOUS PUMP | FALL | [ ] LUBRICATE PUMP MOTOR BEARINGS
PMP | MISCELLANEOUS PUMP | FALL | [ ] VISUALLY INSPECT COUPLING
PMP | MISCELLANEOUS PUMP | FALL | [ ] CLEAN AND INSPECT STRAINER
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK SUPPLY VOLTAGE_____________________
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK MOTOR AMPS_________________________
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK PRESSURES:DISCHARGE_______________
PMP | MISCELLANEOUS PUMP | WINTER | SUCTION_______________
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK FOR SEAL LEAKS
PMP | MISCELLANEOUS PUMP | WINTER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
PMP | MISCELLANEOUS PUMP | WINTER | [ ] ALTERNATE LEAD / LAG PUMP
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK UNUSUAL VIBRATION / NOISE
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK SUPPLY VOLTAGE___________________
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK MOTOR AMPS_______________________
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK PRESSURES: DISCHARGE________________
PMP | MISCELLANEOUS PUMP | SPRING | SUCTION________________
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK FOR SEAL LEAKS
PMP | MISCELLANEOUS PUMP | SPRING | [ ] CHECK MOTOR AND BEARING OIL LEVEL
PMP | MISCELLANEOUS PUMP | SPRING | [ ] ALTERNATE LEAD / LAG PUMP
PMP | MISCELLANEOUS PUMP | SPRING | [ ] LUBRICATE BEARING ASSEMBLY
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK UNUSUAL VIBRATION AND NOISE
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK SUPPLY VOLTAGE______________________
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK MOTOR AMPS__________________________
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK PRESSURES: DISCHARGE_________________
PMP | MISCELLANEOUS PUMP | SUMMER | SUCTION_________________
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK FOR SEAL LEAKS
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] CHECK MOTOR AND BEARING OIL LEVLE
PMP | MISCELLANEOUS PUMP | SUMMER | [ ] ALTERNATE LEAD / LAG PUMP
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
POZ | PRO-SERIES OZONE SYSTEM | FALL | LAST SERVICE AND OPERATING LIMITS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] DIS PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] SUC PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] AIR PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] INSP BACK-FLOW PROTECTION DEVICES
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CHECK FOR WATER OR OZONE LEAKS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] INSP CABINET AIR INTAKE FILTER
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CHECK COOLING FAN OPERATION
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] TEST WATER AND GAS PRESS SAFETY SWITCHES
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CYCLE WATER VALVES (POWER OFF)
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CLEAN ORP PROBE
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CHECK ORP PROBE CALIBRATION
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CHECK ORP PROBE SET POINTS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CLEAN CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CALIBRATE CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *CHECK CONDUCTIVITY CONTROLLER SET POINT
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *TEST OPERATION OF THE BLOWDOWN VALVE
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | FALL | AND SHIP FOR EVALUATION
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] *PERFORM TELOG MONITORING
POZ | PRO-SERIES OZONE SYSTEM | FALL | *IF APPLICABLE
POZ | PRO-SERIES OZONE SYSTEM | FALL | QUARTERLY ADDITIONS TO CHECKLISTS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] INSP COMPRESSOR INTAKE AIR FILTER
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
POZ | PRO-SERIES OZONE SYSTEM | FALL | ANNUAL ADDITIONS TO CHECKLISTS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] TIGHTEN NUTS, SCREWS, FITTINGS AND ELECT CONNECTIONS
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CHECK COMPRESSOR FOR PROPER OPERATION
POZ | PRO-SERIES OZONE SYSTEM | FALL | [ ] CHECK OXYGEN GENERATOR FOR PROPER OPERATION
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
POZ | PRO-SERIES OZONE SYSTEM | WINTER | LAST SERVICE AND OPERATING LIMITS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] DIS PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] SUC PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] AIR PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] INSP BACK-FLOW PROTECTION DEVICES
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK FOR WATER OR OZONE LEAKS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] INSP CABINET AIR INTAKE FILTER
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] CHECK COOLING FAN OPERATION
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] TEST WATER AND GAS PRESS SAFETY SWITCHES
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] CYCLE WATER VALVES (POWER OFF)
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CLEAN ORP PROBE
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CHECK ORP PROBE CALIBRATION
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CHECK ORP PROBE SET POINTS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CLEAN CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CALIBRATE CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *CHECK CONDUCTIVITY CONTROLLER SET POINT
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *TEST OPERATION OF THE BLOWDOWN VALVE
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | AND SHIP FOR EVALUATION
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] *PERFORM TELOG MONITORING
POZ | PRO-SERIES OZONE SYSTEM | WINTER | *IF APPLICABLE
POZ | PRO-SERIES OZONE SYSTEM | WINTER | QUARTERLY ADDITIONS TO CHECKLISTS
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] INSP COMPRESSOR INTAKE AIR FILTER
POZ | PRO-SERIES OZONE SYSTEM | WINTER | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
POZ | PRO-SERIES OZONE SYSTEM | SPRING | LAST SERVICE AND OPERATING LIMITS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] DIS PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] SUC PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] AIR PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] INSP BACK-FLOW PROTECTION DEVICES
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK FOR WATER OR OZONE LEAKS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] INSP CABINET AIR INTAKE FILTER
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] CHECK COOLING FAN OPERATION
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] TEST WATER AND GAS PRESS SAFETY SWITCHES
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] CYCLE WATER VALVES (POWER OFF)
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CLEAN ORP PROBE
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CHECK ORP PROBE CALIBRATION
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CHECK ORP PROBE SET POINTS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CLEAN CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CALIBRATE CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *CHECK CONDUCTIVITY CONTROLLER SET POINT
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *TEST OPERATION OF THE BLOWDOWN VALVE
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | AND SHIP FOR EVALUATION
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] *PERFORM TELOG MONITORING
POZ | PRO-SERIES OZONE SYSTEM | SPRING | *IF APPLICABLE
POZ | PRO-SERIES OZONE SYSTEM | SPRING | QUARTERLY ADDITIONS TO CHECKLISTS
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] INSP COMPRESSOR INTAKE AIR FILTER
POZ | PRO-SERIES OZONE SYSTEM | SPRING | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] VISUALLY INSPECT WATER SYSTEM OPERATION
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK SYSTEM GAUGES, COMPARE AGAINST
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | LAST SERVICE AND OPERATING LIMITS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] DIS PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] SUC PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] AIR PRESS_______________
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] INSP BACK-FLOW PROTECTION DEVICES
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK FOR WATER OR OZONE LEAKS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] INSP CABINET AIR INTAKE FILTER
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] CHECK COOLING FAN OPERATION
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] TEST WATER AND GAS PRESS SAFETY SWITCHES
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] CYCLE WATER VALVES (POWER OFF)
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CLEAN ORP PROBE
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CHECK ORP PROBE CALIBRATION
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CHECK ORP PROBE SET POINTS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CLEAN CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CALIBRATE CONDUCTIVITY PROBE
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *CHECK CONDUCTIVITY CONTROLLER SET POINT
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *TEST OPERATION OF THE BLOWDOWN VALVE
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *REMOVE EXPOSED CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | AND SHIP FOR EVALUATION
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *REPLACE W/FRESH CORROSION MONITORING COUPONS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *TAKE WATER SAMPLES FOR ANALYSIS OR TESTING
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] *PERFORM TELOG MONITORING
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | *IF APPLICABLE
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | QUARTERLY ADDITIONS TO CHECKLISTS
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] INSP COMPRESSOR INTAKE AIR FILTER
POZ | PRO-SERIES OZONE SYSTEM | SUMMER | [ ] CLEAN CABINET INTERIORS (POWER OFF/SEE MANUAL)
PRV | PRESSURE REDUCING VALVE | FALL | [ ] CHECK PRESSURE SETTING
PRV | PRESSURE REDUCING VALVE | FALL | [ ] INSPECT FOR WATER LEAKS
PRV | PRESSURE REDUCING VALVE | FALL | [ ] INSPECT PRESSURE RELIEF FOR LEAKS
PRV | PRESSURE REDUCING VALVE | WINTER | [ ] CHECK PRESSURE SETTING
PRV | PRESSURE REDUCING VALVE | WINTER | [ ] INSPECT FOR WATER LEAKS
PRV | PRESSURE REDUCING VALVE | WINTER | [ ] INSPECT PRESSURE RELIEF FOR LEAKS
PRV | PRESSURE REDUCING VALVE | SPRING | [ ] CHECK PRESSURE SETTING
PRV | PRESSURE REDUCING VALVE | SPRING | [ ] INSPECT FOR WATER LEAKS
PRV | PRESSURE REDUCING VALVE | SPRING | [ ] INSPECT PRESSURE RELIEF FOR LEAKS
PRV | PRESSURE REDUCING VALVE | SUMMER | [ ] CHECK PRESSURE SETTING
PRV | PRESSURE REDUCING VALVE | SUMMER | [ ] INSPECT FOR WATER LEAKS
PRV | PRESSURE REDUCING VALVE | SUMMER | [ ] INSPECT PRESSURE RELIEF FOR LEAKS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | STACK PRESSURE-DROP MONITORING EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK MANOMETER FLUID LEVEL
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK MONITORING EQUIPMENT WITH MAGNAHELIC GAUGE
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK OPERATION OF WARNING LAMPS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | VERTICAL STACK
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK STACK FOR OBSTRUCTIONS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK DUCTWORK FOR CRACKS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | FAN, MOTOR, AND BEARINGS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK FAN AND BEARINGS FOR PRESENCE OF EXCESSIVE DIRT
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] LUBRICATE MOTOR AND BEARINGS AS NECESSARY
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK ALIGNMENT OF BELTS AND PULLEYS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | DRY FILTERS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK THAT ALL FILTERS ARE IN PLACE WITH NO GAPS
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK FILTERS FOR CLEANLINESS (CLEAN OR REPLACE)
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | SPRAY EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK PUMP FOR OPERABILITY
PSB | PAINT/SOLVENT SPRAY BOOTH | FALL | [ ] CHECK AMP DRAW OF PUMP MOTOR
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | STACK PRESSURE-DROP MONITORING EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK MANOMETER FLUID LEVEL
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK MONITORING EQUIPMENT WITH MAGNAHELIC GAUGE
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK OPERATION OF WARNING LAMPS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | VERTICAL STACK
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK STACK FOR OBSTRUCTIONS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK DUCTWORK FOR CRACKS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | FAN, MOTOR, AND BEARINGS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK FAN AND BEARINGS FOR PRESENCE OF EXCESSIVE DIRT
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] LUBRICATE MOTOR AND BEARINGS AS NECESSARY
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK ALIGNMENT OF BELTS & PULLEYS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | DRY FILTERS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK THAT ALL FILTERS ARE IN PLACE WITH NO GAPS
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK FILTERS FOR CLEANLINESS (CLEAN OR REPLACE)
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | SPRAY EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK PUMP FOR OPERABILITY
PSB | PAINT/SOLVENT SPRAY BOOTH | WINTER | [ ] CHECK AMP DRAW OF PUMP MOTOR
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | STACK PRESSURE-DROP MONITORING EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK MANOMETER FLUID LEVEL
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK MONITORING EQUIPMENT WITH MAGNAHELIC GAUGE
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK OPERATION OF WARNING LAMPS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | VERTICAL STACK
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK STACK FOR OBSTRUCTIONS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK DUCTWORK FOR CRACKS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | FAN, MOTOR, AND BEARINGS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK FAN AND BEARINGS FOR PRESENCE OF EXCESSIVE DIRT
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] LUBRICATE MOTOR AND BEARINGS AS NECESSARY
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK ALIGNMENT OF BELTS AND PULLEYS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | DRY FILTERS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK THAT ALL FILTERS ARE IN PLACE WITH NO GAPS
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK FILTERS FOR CLEANLINESS (CLEAN OR REPLACE)
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | SPRAY EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK PUMP FOR OPERABILITY
PSB | PAINT/SOLVENT SPRAY BOOTH | SPRING | [ ] CHECK AMP DRAW OF PUMP MOTOR
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | STACK PRESSURE-DROP MONITORING EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK MANOMETER FLUID LEVEL
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK MONITORING EQUIPMENT WITH MAGNAHELIC GAUGE
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK OPERATION OF WARNING LAMPS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | VERTICAL STACK
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK STACK FOR OBSTRUCTIONS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK DUCTWORK FOR CRACKS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | FAN, MOTOR, AND BEARINGS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK FAN AND BEARINGS FOR PRESENCE OF EXCESSIVE DIRT
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] LUBRICATE MOTOR AND BEARINGS AS NECESSARY
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK ALIGNMENT OF BELTS AND PULLEYS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | DRY FILTERS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK THAT ALL FILTERS ARE IN PLACE WITH NO GAPS
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK FILTERS FOR CLEANLINESS (CLEAN OR REPLACE)
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | SPRAY EQUIPMENT
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK PUMP FOR OPERABILITY
PSB | PAINT/SOLVENT SPRAY BOOTH | SUMMER | [ ] CHECK AMP DRAW OF PUMP MOTOR
RC | ROTO CLONE | FALL | [ ] CHECK OPERATION
RC | ROTO CLONE | FALL | [ ] CHECK VOLTS
RC | ROTO CLONE | FALL | [ ] CHECK AMPS
RC | ROTO CLONE | FALL | [ ] CHECK PULLEY WEAR
RC | ROTO CLONE | FALL | [ ] CHECK BELTS
RC | ROTO CLONE | FALL | [ ] CHECK DRIVE BEARINGS
RC | ROTO CLONE | FALL | [ ] CHECK SEAL BEARINGS
RC | ROTO CLONE | FALL | [ ] LUBE BEARINGS AS PER MFGR. SPECS
RC | ROTO CLONE | FALL | WASH CYCLE (IF APPLICABLE)
RC | ROTO CLONE | FALL | [ ] CHECK DRAINS
RC | ROTO CLONE | FALL | [ ] CHECK WASHING CYCLE
RC | ROTO CLONE | FALL | [ ] CHECK SPRAY NOZZLES
RC | ROTO CLONE | FALL | [ ] CHECK SPRAY NOZZLE FLOW
RC | ROTO CLONE | WINTER | [ ] CHECK OPERATION
RC | ROTO CLONE | WINTER | [ ] CHECK VOLTS
RC | ROTO CLONE | WINTER | [ ] CHECK AMPS
RC | ROTO CLONE | WINTER | [ ] CHECK PULLEY WEAR
RC | ROTO CLONE | WINTER | [ ] CHECK BELTS
RC | ROTO CLONE | WINTER | [ ] CHECK DRIVE BEARINGS
RC | ROTO CLONE | WINTER | [ ] CHECK SEAL BEARINGS
RC | ROTO CLONE | WINTER | [ ] LUBE BEARINGS AS PER MFGR SPECS
RC | ROTO CLONE | WINTER | WASH CYCLE (IF APPLICABLE)
RC | ROTO CLONE | WINTER | [ ] CHECK DRAINS
RC | ROTO CLONE | WINTER | [ ] CHECK WASHING CYCLE
RC | ROTO CLONE | WINTER | [ ] CHECK SPRAY NOZZLES
RC | ROTO CLONE | WINTER | [ ] CHECK SPRAY NOZZLE FLOW
RC | ROTO CLONE | SPRING | [ ] CHECK OPERATION
RC | ROTO CLONE | SPRING | [ ] CHECK VOLTS
RC | ROTO CLONE | SPRING | [ ] CHECK AMPS
RC | ROTO CLONE | SPRING | [ ] CHECK PULLEY WEAR
RC | ROTO CLONE | SPRING | [ ] CHECK BELTS
RC | ROTO CLONE | SPRING | [ ] CHECK DRIVE BEARINGS
RC | ROTO CLONE | SPRING | [ ] CHECK SEAL BEARINGS
RC | ROTO CLONE | SPRING | [ ] LUBE BEARINGS AS PER MFGR SPECS
RC | ROTO CLONE | SPRING | WASHING CYCLE (IF APPLICABLE)
RC | ROTO CLONE | SPRING | [ ] CHECK DRAINS
RC | ROTO CLONE | SPRING | [ ] CHECK WASHING CYCLE
RC | ROTO CLONE | SPRING | [ ] CHECK SPRAY NOZZLES
RC | ROTO CLONE | SPRING | [ ] CHECK SPRAY NOZZLE FLOW
RC | ROTO CLONE | SUMMER | [ ] CHECK OPERATION
RC | ROTO CLONE | SUMMER | [ ] CHECK VOLTS
RC | ROTO CLONE | SUMMER | [ ] CHECK AMPS
RC | ROTO CLONE | SUMMER | [ ] CHECK PULLEY WEAR
RC | ROTO CLONE | SUMMER | [ ] CHECK BELTS
RC | ROTO CLONE | SUMMER | [ ] CHECK DRIVE BEARINGS
RC | ROTO CLONE | SUMMER | [ ] CHECK SEAL BEARINGS
RC | ROTO CLONE | SUMMER | [ ] LUBE BEARINGS AS PER MFGR SPECS
RC | ROTO CLONE | SUMMER | WASH CYCLE (IF APPLICABLE)
RC | ROTO CLONE | SUMMER | [ ] CHECK DRAINS
RC | ROTO CLONE | SUMMER | [ ] CHECK WASHING CYCLE
RC | ROTO CLONE | SUMMER | [ ] CHECK SPRAY NOZZLE
RC | ROTO CLONE | SUMMER | [ ] CHECK SPRAY NOZZLE FLOW
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK COMPRESSOR OIL LEVELS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
RCH | RECIPROCATING CHILLER | FALL | LOAD CONDITION:
RCH | RECIPROCATING CHILLER | FALL | A. DISCHARGE LINE TEMPERATURE:
RCH | RECIPROCATING CHILLER | FALL | COMP #1 ________DEG.F COMP #2 ________DEG.F
RCH | RECIPROCATING CHILLER | FALL | COMP #3 ________DEG.F COMP #4 ________DEG.F
RCH | RECIPROCATING CHILLER | FALL | B. OUTSIDE AIR TEMP: ________DEG.F
RCH | RECIPROCATING CHILLER | FALL | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | FALL | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK OUTDOOR COIL CONDITION
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK FAN BELTS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK HOT GAS BY-PASS OPERATION
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK CRANKCASE HEATERS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHANGE LEAD COMPRESSOR
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK SEQUENCE OF OPERATION
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASSES
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK CONTROL SETPOINTS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK ALL MOTORS AMPS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK SUPPLY VOLTAGE______,______,______.
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK CAPACITY CONTROLS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK SAFETY CONTROLS
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
RCH | RECIPROCATING CHILLER | FALL | OUTLET________PSI
RCH | RECIPROCATING CHILLER | FALL | [ ] RECORD INFORMATION IN CUSTOMERS LOG BOOK
RCH | RECIPROCATING CHILLER | FALL | [ ] CHECK CHILLED WATER FREEZE POINT ___________DEG.
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK COMPRESSOR OIL LEVELS:
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
RCH | RECIPROCATING CHILLER | WINTER | LOAD CONDITION:
RCH | RECIPROCATING CHILLER | WINTER | A. DISCHARGE LINE TEMP:
RCH | RECIPROCATING CHILLER | WINTER | COMP #1 ________DEG.F COMP #2 ________DEG.F
RCH | RECIPROCATING CHILLER | WINTER | COMP #3 ________DEG.F COMP #4 ________DEG.F
RCH | RECIPROCATING CHILLER | WINTER | B. OUTSIDE AIR TEMP: _________DEG.F
RCH | RECIPROCATING CHILLER | WINTER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | WINTER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK OUTDOOR COIL CONDITION
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK FAN BELTS
RCH | RECIPROCATING CHILLER | WINTER | [ ] LUBRICATE FAN BEARINGS
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK CRANKCASE HEATERS
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHANGE LEAD COMPRESSOR
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASSES
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK CONTROL SET POINTS
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK ALL MOTORS AMPS
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
RCH | RECIPROCATING CHILLER | WINTER | OUTLET________PSI
RCH | RECIPROCATING CHILLER | WINTER | [ ] CHECK GLYCOL IF REQUIRED_________________DEG F.
RCH | RECIPROCATING CHILLER | WINTER | [ ] RECORD INFORMATION IN CUSTOMERS LOG BOOK
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK COMPRESSOR OIL LEVELS:
RCH | RECIPROCATING CHILLER | SPRING | [ ] OIL SAMPLE #1_____#2_____#3_____#4_____
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
RCH | RECIPROCATING CHILLER | SPRING | LOAD CONDITION:
RCH | RECIPROCATING CHILLER | SPRING | A. DISCHARGE PRESSURE:
RCH | RECIPROCATING CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | B. SUCTION PRESSURE:
RCH | RECIPROCATING CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | C. NET OIL PRESSURE:
RCH | RECIPROCATING CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
RCH | RECIPROCATING CHILLER | SPRING | D. CIRCUIT SUPERHEAT:
RCH | RECIPROCATING CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | E. SYSTEM SUBCOOLING:
RCH | RECIPROCATING CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | F. DISCHARGE LINE TEMPERATURE:
RCH | RECIPROCATING CHILLER | SPRING | COMP #1 ________DEG.F COMP #2 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | COMP #3 ________DEG.F COMP #4 ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | G. OUTSIDE AIR TEMP: ________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | H. CHILLED WTR TEMP: IN________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | OUT________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | I. CONDENSER WATER TEMP: IN________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | OUT________DEG.F
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK OUTDOOR COIL CONDITION
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK OUTDOOR FANS CONDITION
RCH | RECIPROCATING CHILLER | SPRING | [ ] LUBRICATE FAN BEARINGS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK FAN BELT
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK OUTDOOR FAN MOTORS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CONDENSER FAN CYCLE
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK TXV SENSING BULBS FOR CLEANLINESS & CONTACT
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CRANKCASE HEATERS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHANGE LEAD COMPRESSOR
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK SEQUENCE OF OPERATION
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASSES
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CONTROL SET POINTS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK ALL MOTORS AMPS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK SUPPLY VOLTAGE______,______,______.
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CAPACITY CONTROLS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK SAFETY CONTROLS
RCH | RECIPROCATING CHILLER | SPRING | FREEZE PROTECTION____________
RCH | RECIPROCATING CHILLER | SPRING | OIL FAILURE_____________
RCH | RECIPROCATING CHILLER | SPRING | LOW AND HIGH PRESSURE_____________
RCH | RECIPROCATING CHILLER | SPRING | FLOW SWITCH__________________
RCH | RECIPROCATING CHILLER | SPRING | [ ] MEG OHM MOTOR 10 HP OR LARGER
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CONTACTOR POINTS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK CHILLED WTR PRESS: IN________PSI
RCH | RECIPROCATING CHILLER | SPRING | OUT________PSI
RCH | RECIPROCATING CHILLER | SPRING | [ ] INSPECT RELIEF VALVE
RCH | RECIPROCATING CHILLER | SPRING | [ ] CHECK STARTER OVERLOADS AND TIME DELAYS
RCH | RECIPROCATING CHILLER | SPRING | [ ] RECORD INFORMATION IN CUSTOMERS LOG
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK COMPRESSOR OIL LEVELS:
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
RCH | RECIPROCATING CHILLER | SUMMER | LOAD CONDITION:
RCH | RECIPROCATING CHILLER | SUMMER | A. DISCHARGE LINE TEMPERATURE:
RCH | RECIPROCATING CHILLER | SUMMER | COMP #1 ________DEG.F COMP #2 ________DEG.F
RCH | RECIPROCATING CHILLER | SUMMER | COMP #3 ________DEG.F COMP #4 ________DEG.F
RCH | RECIPROCATING CHILLER | SUMMER | B. OUTSIDE AIR TEMP: ________DEG.F
RCH | RECIPROCATING CHILLER | SUMMER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | SUMMER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK OUTDOOR COIL CONDITION
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK FAN BELTS
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK CRANKCASE HEATERS
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHANGE LEAD COMPRESSOR
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASSES
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK CONTROL SET POINTS
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK ALL MOTORS AMPS
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCH | RECIPROCATING CHILLER | SUMMER | [ ] CHECK CHILLED WTR PRESS. IN________PSI
RCH | RECIPROCATING CHILLER | SUMMER | OUT________PSI
RCH | RECIPROCATING CHILLER | SUMMER | [ ] RECORD INFORMATION IN CUSTOMER LOG BOOK
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK BELTS
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK PULLEY WEAR
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK COIL CONDITION
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK SUPPLY VOLTAGE____________________________-
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK MOTOR AMPS_________________________________
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK CRANKCASE HEATER
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK OIL LEVEL
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK COOLING SEQUENCE OF OPERATION
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK DISCHARGE TEMPERATURE_________________DEG F.
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK SUB COOLING________________________________
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE______________
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK SAFETIES
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] INSPECT FAN BLADES AND SUPPORTS
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK SAFETY OPERATION AND SETTING
RCU | REFRIGERATION CONDENSING UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK BELTS
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK PULLEY WEAR
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK COIL CONDITION
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK CRANKCASE HEATER
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK DISCHARGE TEMPERATURE______________DEG F.
RCU | REFRIGERATION CONDENSING UNIT | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK BELTS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK PULLEY WEAR
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK COIL CONDITION
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE________________________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK MOTOR AMPS___________________________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK OIL LEVEL
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK COOLING SEQUENCE OF OPERATION
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK DISCHARGE TEMPERATURE_____________DEG F.
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SUB COOLING________________________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE___________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK CAPACITY CONTROL
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SAFETIES
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK DISCHARGE PRESSURE____________________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SUCTION PRESSURE_____________________
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK CONTROL POINTS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] INSPECT FAN BLADES AND SUPPORTS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK SAFETY OPERATION AND SETTING
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] INSPECT CONTACTOR POINTS
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
RCU | REFRIGERATION CONDENSING UNIT | SPRING | [ ] OIL TEST SEMI HERMETICS
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK BELTS
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK PULLEY WEAR
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK COIL CONDITION
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK SUPPLY VOLTAGE_______________________
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK MOTOR AMPS___________________________
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK OIL LEVEL
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK COOLING SEQUENCE OF OPERATION
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK DISCHARGE TEMPERATURE___________DEG F.
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK SUB COOLING
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE____________
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK CAPACITY CONTROL
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK SAFETIES
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK DISCHARGE PRESSURE_____________________
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK SUCTION PRESSURE______________________
RCU | REFRIGERATION CONDENSING UNIT | SUMMER | [ ] CHECK HEAD PRESSURE CONTROL OPERATION
RD | ROOF DRAIN | FALL | [ ] INSPECT ROOF DRAIN FOR OBSTRUCTION
RD | ROOF DRAIN | FALL | [ ] CLEAN DRAIN OBSTRUCTIONS
RD | ROOF DRAIN | FALL | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
RD | ROOF DRAIN | WINTER | [ ] INSPECT ROOF DRAIN FOR OBSTRUCTIONS
RD | ROOF DRAIN | WINTER | [ ] CLEAN DRAIN OBSTRUCTIONS
RD | ROOF DRAIN | WINTER | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
RD | ROOF DRAIN | SPRING | [ ] INSPECT ROOF DRAIN FOR OBSTRUCTION
RD | ROOF DRAIN | SPRING | [ ] CLEAN DRAIN OBSTRUCTION
RD | ROOF DRAIN | SPRING | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
RD | ROOF DRAIN | SUMMER | [ ] INSPECT ROOF DRAIN FOR OBSTRUCTION
RD | ROOF DRAIN | SUMMER | [ ] CLEAN DRAIN OBSTRUCTIONS
RD | ROOF DRAIN | SUMMER | [ ] REPORT DRAIN PROBLEMS TO BUILDING OWNER
REH | RADIANT ELECTRIC HEATER | FALL | [ ] CHECK ELEMENT CONDITION
REH | RADIANT ELECTRIC HEATER | FALL | [ ] CHECK WIRING
REH | RADIANT ELECTRIC HEATER | FALL | [ ] CHECK LIMITS AND SAFETIES
REH | RADIANT ELECTRIC HEATER | FALL | [ ] CHECK OPERATION
REH | RADIANT ELECTRIC HEATER | WINTER | [ ] CHECK ELEMENT CONDITION
REH | RADIANT ELECTRIC HEATER | WINTER | [ ] CHECK WIRING
REH | RADIANT ELECTRIC HEATER | WINTER | [ ] CHECK LIMITS AND SAFETIES
REH | RADIANT ELECTRIC HEATER | WINTER | [ ] CHECK OPERATION
REH | RADIANT ELECTRIC HEATER | SPRING | [ ] CHECK ELEMENT CONDITION
REH | RADIANT ELECTRIC HEATER | SPRING | [ ] CHECK WIRING
REH | RADIANT ELECTRIC HEATER | SPRING | [ ] CHECK LIMITS AND SAFETIES
REH | RADIANT ELECTRIC HEATER | SPRING | [ ] CHECK OPERATION
REH | RADIANT ELECTRIC HEATER | SUMMER | [ ] CHECK ELEMENT CONDITION
REH | RADIANT ELECTRIC HEATER | SUMMER | [ ] CHECK WIRING
REH | RADIANT ELECTRIC HEATER | SUMMER | [ ] CHECK LIMITS AND SAFETIES
REH | RADIANT ELECTRIC HEATER | SUMMER | [ ] CHECK OPERATION
RF | RETURN FAN | FALL | [ ] CHECK BELTS
RF | RETURN FAN | FALL | [ ] CHECK PULLEY ALIGNMENT
RF | RETURN FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RF | RETURN FAN | FALL | [ ] CHECK PULLEY WEAR
RF | RETURN FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
RF | RETURN FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RF | RETURN FAN | FALL | [ ] CHECK CONTACTOR/STARTER POINTS
RF | RETURN FAN | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
RF | RETURN FAN | WINTER | [ ] CHECK BELTS
RF | RETURN FAN | WINTER | [ ] CHECK PULLEY ALIGNMENT
RF | RETURN FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RF | RETURN FAN | WINTER | [ ] CHECK PULLEY WEAR
RF | RETURN FAN | WINTER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
RF | RETURN FAN | WINTER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RF | RETURN FAN | SPRING | [ ] CHECK BELTS
RF | RETURN FAN | SPRING | [ ] CHECK PULLEY ALIGNMENT
RF | RETURN FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RF | RETURN FAN | SPRING | [ ] CHECK PULLEY WEAR
RF | RETURN FAN | SPRING | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
RF | RETURN FAN | SPRING | [ ] LUBRIACTE BLOWER BEARINGS (PER MFG SPECS)
RF | RETURN FAN | SPRING | ON ALL THREE PHASE MOTORS:
RF | RETURN FAN | SPRING | [ ] CHECK AMPS L1_____L2_____L3_____
RF | RETURN FAN | SPRING | [ ] CHECK VOLTAGE L1_____l2_____l3_____
RF | RETURN FAN | SUMMER | [ ] CHECK BELTS
RF | RETURN FAN | SUMMER | [ ] CHECK PULLEY ALIGNMENT
RF | RETURN FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RF | RETURN FAN | SUMMER | [ ] CHECK PULLEY WEAR
RF | RETURN FAN | SUMMER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
RF | RETURN FAN | SUMMER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RLF | RELIEF FAN | FALL | [ ] CHECK BELTS
RLF | RELIEF FAN | FALL | [ ] CHECK PULLEY FOR WEAR
RLF | RELIEF FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RLF | RELIEF FAN | FALL | [ ] CHECK OPERATION
RLF | RELIEF FAN | FALL | [ ] CHECK AMPS____________________
RLF | RELIEF FAN | FALL | [ ] CHECK VOLTAGE____________________
RLF | RELIEF FAN | FALL | [ ] INSPECT BLOWER FOR DIRT
RLF | RELIEF FAN | FALL | [ ] CHECK FAN CAPACITY CONTROL OPERATION
RLF | RELIEF FAN | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
RLF | RELIEF FAN | FALL | [ ] CHECK CONTACTOR POINTS
RLF | RELIEF FAN | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
RLF | RELIEF FAN | FALL | [ ] MEG OHM MOTOR (10HP OR LARGER)
RLF | RELIEF FAN | FALL | [ ] LUBRICATE MOTOR BEARINS (PER MFG SPECS)
RLF | RELIEF FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (SEE MFG SPECS)
RLF | RELIEF FAN | FALL | [ ] INSPECT SPRING ISOLATION
RLF | RELIEF FAN | FALL | [ ] INSPECT FLEX CONNECTOR OR FAN SEAL
RLF | RELIEF FAN | WINTER | [ ] CHECK BELTS
RLF | RELIEF FAN | WINTER | [ ] CHECK PULLEY FOR WEAR
RLF | RELIEF FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RLF | RELIEF FAN | WINTER | [ ] CHECK OPERATION
RLF | RELIEF FAN | WINTER | [ ] CHECK AMPS_______________-
RLF | RELIEF FAN | WINTER | [ ] CHECK VOLTAGE_______________
RLF | RELIEF FAN | WINTER | [ ] INSPECT BLOWER FOR DIRT
RLF | RELIEF FAN | WINTER | [ ] CHECK FAN CAPACITY CONTROL OPERATION
RLF | RELIEF FAN | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RLF | RELIEF FAN | SPRING | [ ] CHECK BELTS
RLF | RELIEF FAN | SPRING | [ ] CHECK PULLEY FOR WEAR
RLF | RELIEF FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RLF | RELIEF FAN | SPRING | [ ] CHECK OPERATION
RLF | RELIEF FAN | SPRING | [ ] CHECK AMPS____________________
RLF | RELIEF FAN | SPRING | [ ] CHECK VOLTAGE____________________
RLF | RELIEF FAN | SPRING | [ ] INSPECT BLOWER FOR DIRT
RLF | RELIEF FAN | SPRING | [ ] CHECK FAN CAPACITY CONTROL OPERATION
RLF | RELIEF FAN | SUMMER | [ ] CHECK BELTS
RLF | RELIEF FAN | SUMMER | [ ] CHECK PULLEY FOR WEAR
RLF | RELIEF FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
RLF | RELIEF FAN | SUMMER | [ ] CHECK OPERATION
RLF | RELIEF FAN | SUMMER | [ ] CHECK AMPS_____________________
RLF | RELIEF FAN | SUMMER | [ ] CHECK VOLTAGE___________________
RLF | RELIEF FAN | SUMMER | [ ] INSPECT BLOWER FOR DIRT
RLF | RELIEF FAN | SUMMER | [ ] CHECK FAN CAPACITY CONTROL OPERATION
RM | REFRIGERANT MONITOR | FALL | [ ] CHECK OPERATION SEQUENCE
RM | REFRIGERANT MONITOR | FALL | [ ] CHECK ALARM OUTPUT
RM | REFRIGERANT MONITOR | FALL | [ ] CHECK CALIBRATION OF SENSORS
RM | REFRIGERANT MONITOR | WINTER | [ ] CHECK OPERATION SEQUENCE
RM | REFRIGERANT MONITOR | SPRING | [ ] CHECK OPERATION SEQUENCE
RM | REFRIGERANT MONITOR | SUMMER | [ ] CHECK OPERATION SEQUENCE
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK COIL CONDITION
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK SUPPLY VOLTAGE________________
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK AMPS__________________
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK OPERATING DISCHARGE PRESSURE_________
ROF | REFRIGERATOR OR FREEZER | FALL | SUCTION PRESSURE_________
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK OIL LEVEL
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK CRANKCASE HEATER
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK COOLING SEQUENCE OF OPERATION
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK TEMP CONTROL/PRESSURE CONTROL OPERATION
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK CAPACITY CONTROL
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] INSPECT DOOR GASKETS
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] INSPECT CONDENDATE PAN AND DRAIN
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK CONDENSATE PAN AND DRAIN HEATER OPERATION
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK DEFROST TIMER
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK DEFROST OPERATION
ROF | REFRIGERATOR OR FREEZER | FALL | [ ] CHECK WATER REGULATING VALVE (IF EQUIPPED)
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK COIL CONDITION
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK SUPPLY VOLTAGE_______________
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK AMPS___________________
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK OPERATING DISCHARGE PRESSURE_______
ROF | REFRIGERATOR OR FREEZER | WINTER | SUCTION PRESSURE_______
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK OIL LEVLE
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK CRANKCASE HEATER
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK COOLING SEQUENCE OF OPERATION
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK TEMP CONTROL/PRESSURE CONTROL OPERATION
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK CAPACITY CONTROL
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] INSPECT DOOR GASKETS
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] INSPECT CONDENSATE PAN AND DRAIN
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK CONDENSATE PAN AND DRAIN HEATER OPERATION
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK DEFROST TIMER
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK DEFROST OPERATION
ROF | REFRIGERATOR OR FREEZER | WINTER | [ ] CHECK WATER REGULATING VALVE (IF EQUIPPED)
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK COIL CONDITION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK SUPPLY VOLTAGE__________________
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK AMPS____________________________
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK OPERATING DISCHARGE PRESSURE______
ROF | REFRIGERATOR OR FREEZER | SPRING | SUCTION PRESSURE______
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK OIL LEVEL
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK CRANKCASE HEATER
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK COOLING SEQUENCE OF OPERATION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK TEMP CONTROL/PRESSURE CONTROL OPERATION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK CAPACITY CONTROL
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] INSPECT DOOR GASKETS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] INSPECT CONDENSATE PAN AND DRAIN
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK CONDENSATE PAN AND DRAIN HEATER OPERATION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK DEFROST TIMER
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK DEFROST OPERATION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK WATER REGULATING VALVE IF EQUIPPED
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] INSPECT BLOWER BLADES AND SUPPORTS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK SUPER HEAT
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK SUB COOLING
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK CONTACTOR POINTS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] MEG OHM MOTOR (10HP OR LARGER)
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] CHECK REFRIGERATION SYSTEM SAFETY
ROF | REFRIGERATOR OR FREEZER | SPRING | SETTING AND OPERATION
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] OIL TEST SEMI HERMETIC COMPRESSORS
ROF | REFRIGERATOR OR FREEZER | SPRING | [ ] LUBRICATE CONDENSER FANS IF REQUIRED
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK COIL CONDITION
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK SUPPLY VOLTAGE____________________
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK AMPS_______________________________
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK OPERATING DISCHARGE PRESSURE_______
ROF | REFRIGERATOR OR FREEZER | SUMMER | SUCTION PRESSURE_______
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK OIL LEVEL
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK CRANKCASE HEATER
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK COOLING SEQUENCE OF OPERATION
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK TEMP CONTROL/PRESSURE CONTROL OPERATION
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK CAPACITY CONTROL
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] INSPECT DOOR GASKETS
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] INSPECT CONDENSATE PAN AND DRAIN
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK CONDENSATE PAN AND DRAIN HEATER OPERATION
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK DEFROST TIMER
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK DEFROST OPERATION
ROF | REFRIGERATOR OR FREEZER | SUMMER | [ ] CHECK WATER REGULATING VALVE IF EQUIPPED
RP | RECLAIM PUMP | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RP | RECLAIM PUMP | FALL | [ ] CHECK VOLTAGE________________
RP | RECLAIM PUMP | FALL | [ ] CHECK AMPS___________________
RP | RECLAIM PUMP | FALL | [ ] CHECK PRESSURE DISCHARGE________SUCTION__________
RP | RECLAIM PUMP | FALL | [ ] CHECK FOR WATER LEAKS
RP | RECLAIM PUMP | FALL | [ ] CHECK CONTROL OPERATION
RP | RECLAIM PUMP | FALL | [ ] INSPECT COUPLER
RP | RECLAIM PUMP | FALL | [ ] CHECK BEARING ASSEMBLY OIL
RP | RECLAIM PUMP | FALL | [ ] LUBRICATE PUMP MOTOR BEARINGS (PER MFG SPECS)
RP | RECLAIM PUMP | FALL | [ ] CHECK ELECTRICAL CONNECTION
RP | RECLAIM PUMP | FALL | [ ] CHECK CONTACTOR POINTS
RP | RECLAIM PUMP | FALL | [ ] INSPECT AND CLEAN STRAINER
RP | RECLAIM PUMP | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RP | RECLAIM PUMP | WINTER | [ ] CHECK VOLTAGE_________________
RP | RECLAIM PUMP | WINTER | [ ] CHECK AMPS____________________
RP | RECLAIM PUMP | WINTER | [ ] CHECK PRESSURE DISCHARGE_______________
RP | RECLAIM PUMP | WINTER | SUCTION_______________
RP | RECLAIM PUMP | WINTER | [ ] CHECK FOR WATER LEAKS
RP | RECLAIM PUMP | WINTER | [ ] CHECK CONTROL OPERATION
RP | RECLAIM PUMP | WINTER | [ ] INSPECT COUPLER
RP | RECLAIM PUMP | WINTER | [ ] CHECK BEARING ASSEMBLY OIL
RP | RECLAIM PUMP | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RP | RECLAIM PUMP | SPRING | [ ] CHECK VOLTAGE_____________
RP | RECLAIM PUMP | SPRING | [ ] CHECK AMPS_______________
RP | RECLAIM PUMP | SPRING | [ ] CHECK PRESSURE DISCHARGE_______________
RP | RECLAIM PUMP | SPRING | SUCTION_______________
RP | RECLAIM PUMP | SPRING | [ ] CHECK FOR WATER LEAKS
RP | RECLAIM PUMP | SPRING | [ ] CHECK CONTROL OPERATION
RP | RECLAIM PUMP | SPRING | [ ] INSPECT COUPLER
RP | RECLAIM PUMP | SPRING | [ ] CHECK BEARING ASSEMBLY OIL
RP | RECLAIM PUMP | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
RP | RECLAIM PUMP | SUMMER | [ ] CHECK VOLTAGE____________
RP | RECLAIM PUMP | SUMMER | [ ] CHECK AMPS________________
RP | RECLAIM PUMP | SUMMER | [ ] CHECK PRESSURE DISCHARGE______________
RP | RECLAIM PUMP | SUMMER | SUCTION______________
RP | RECLAIM PUMP | SUMMER | [ ] CHECK FOR WATER LEAKS
RP | RECLAIM PUMP | SUMMER | [ ] CHECK CONTROL OPERATION
RP | RECLAIM PUMP | SUMMER | [ ] INSPECT COUPLER
RP | RECLAIM PUMP | SUMMER | [ ] CHECK BEARING ASSEMBLY OIL
RTH | RADIANT TUBE HEATER | FALL | [ ] CHECK MANIFOLD GAS PRESSURE_________" WC
RTH | RADIANT TUBE HEATER | FALL | [ ] CHECK BURNER OPERATION
RTH | RADIANT TUBE HEATER | FALL | [ ] CHECK COMBUSTION BLOWER WHEEL AND MOTOR
RTH | RADIANT TUBE HEATER | FALL | [ ] CHECK IGNITOR
RTH | RADIANT TUBE HEATER | FALL | [ ] CHECK OPERATING CYCLE
RTH | RADIANT TUBE HEATER | WINTER | [ ] CHECK HEAT OPERATION
RTH | RADIANT TUBE HEATER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION
RTH | RADIANT TUBE HEATER | SPRING | [ ] CHECK HEAT OPERATION
RTH | RADIANT TUBE HEATER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION
RTH | RADIANT TUBE HEATER | SUMMER | [ ] CHECK HEAT OPERATION
RTH | RADIANT TUBE HEATER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK BELTS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
RTU | ROOFTOP UNIT | FALL | [ ] ADD PAN TABS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK UNUSUAL VIBRATION/NOISE
RTU | ROOFTOP UNIT | FALL | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SUPPLY VOLTAGE_________,__________,__________.
RTU | ROOFTOP UNIT | FALL | [ ] SUPPLY MOTOR AMPS #1____,____,____#2____,____,____.
RTU | ROOFTOP UNIT | FALL | #3____,____,____#4____,____,____.
RTU | ROOFTOP UNIT | FALL | [ ] RETURN MOTOR AMPS #1____,____,____#2____,____,____.
RTU | ROOFTOP UNIT | FALL | [ ] CHECK INDOOR COIL TEMP.DROP___________DEG. F
RTU | ROOFTOP UNIT | FALL | [ ] CHECK COMPRESSOR DISCH.TEMP #1____#2____#3____#4____
RTU | ROOFTOP UNIT | FALL | [ ] CHECK ECONOMIZER OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK RELIEF DAMPERS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK CONTROL SET POINTS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK CRANKCASE HEATER
RTU | ROOFTOP UNIT | FALL | [ ] CHECK OIL LEVEL
RTU | ROOFTOP UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RTU | ROOFTOP UNIT | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
RTU | ROOFTOP UNIT | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK PULLEY WEAR
RTU | ROOFTOP UNIT | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
RTU | ROOFTOP UNIT | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
RTU | ROOFTOP UNIT | FALL | BINDING AND LUBE
RTU | ROOFTOP UNIT | FALL | [ ] LUBRICATE INLET VANE PIVOT POINTS
RTU | ROOFTOP UNIT | FALL | [ ] LUBRICATE PIVOT POINTS
RTU | ROOFTOP UNIT | FALL | [ ] CHECK FRESH AIR SCREENS AND CLEAN AS NEEDED
RTU | ROOFTOP UNIT | FALL | ELECTRIC HEAT: (IF EQUIPPED)
RTU | ROOFTOP UNIT | FALL | [ ] CHECK AMP DRAW_____,_____,_____.
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SEQUENCER OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK TEMPERATURE RISE_______________DEG.F
RTU | ROOFTOP UNIT | FALL | GAS HEAT: (IF EQUIPPED)
RTU | ROOFTOP UNIT | FALL | [ ] CHECK TEMPERATURE RISE________________DEG. F
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SEQUENCER OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK FAN SWITCH
RTU | ROOFTOP UNIT | FALL | [ ] VISUAL INSPECTION OF HEAT EXCHANGERS AND
RTU | ROOFTOP UNIT | FALL | VISUAL CHECK OF FLUE
RTU | ROOFTOP UNIT | FALL | [ ] CHECK PILOT SETTING________________"WC
RTU | ROOFTOP UNIT | FALL | [ ] CHECK MAIN LINE GAS PRESSURE_____________"WC
RTU | ROOFTOP UNIT | FALL | [ ] CHECK MANIFOLD GAS PRESSURE_______________"WC
RTU | ROOFTOP UNIT | FALL | [ ] CLEAN COMBUSTION BLOWER WHEEL
RTU | ROOFTOP UNIT | FALL | [ ] OIL COMBUSTION BLOWER MOTOR
RTU | ROOFTOP UNIT | FALL | [ ] CLEAN AND ADJUST IGNITOR
RTU | ROOFTOP UNIT | FALL | EVAPORATIVE CONDENSER
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SUMP CONDITION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SPRAY PUMP OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] DRAIN AND SECURE PUMP IF REQUIRED
RTU | ROOFTOP UNIT | FALL | [ ] CHECK AUTO FILL VALVE OPERATION
RTU | ROOFTOP UNIT | FALL | [ ] CHECK SUMP HEATER
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK BELTS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
RTU | ROOFTOP UNIT | WINTER | [ ] ADD PAN TABS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK UNUSUAL VIBRATION/NOISE
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SUPPLY MOTOR AMPS #1___,___,___#2___,___,___
RTU | ROOFTOP UNIT | WINTER | #3___,___,___#4___,___,___
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK RETURN MOTOR AMPS #1___,___,___#2___,___,___
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK ECONOMIZER OPERATION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK RELIEF DAMPERS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK CONTROL SET POINTS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK CRANKCASE HEATER
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK OIL LEVEL
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK FRESH AIR INTAKE SCREENS
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK HOT GAS BYPASS OPERATION
RTU | ROOFTOP UNIT | WINTER | [ ] LUBRICATE DAMPER PIVOT POINTS
RTU | ROOFTOP UNIT | WINTER | [ ] LUBRICATE INLET VANE PIVOT POINTS
RTU | ROOFTOP UNIT | WINTER | ELECTRIC HEAT: (IF EQUIPPED)
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
RTU | ROOFTOP UNIT | WINTER
RTU | ROOFTOP UNIT | WINTER | GAS HEAT: (IF EQUIPPED)
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
RTU | ROOFTOP UNIT | WINTER | EVAPORATIVE CONDENSER
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SUMP CONDITION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SPRAY PUMP OPERATION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK AUTO FILL VALVE OPERATION
RTU | ROOFTOP UNIT | WINTER | [ ] CHECK SUMP HEATER
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK BELTS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
RTU | ROOFTOP UNIT | SPRING | [ ] ADD PAN TABS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK UNUSUAL VIBRATION/NOISE
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE______,______,______
RTU | ROOFTOP UNIT | SPRING | [ ] SUPPLY MOTOR AMPS #1____,____,____#2____,____,____
RTU | ROOFTOP UNIT | SPRING | #3____,____,____#4____,____,____
RTU | ROOFTOP UNIT | SPRING | [ ] RETURN MOTOR AMPS #1____,____,____#2____,____,____
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK ECONOMIZER OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK RELIEF DAMPERS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CONTROL SET POINTS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK OIL LEVEL
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK INDOOR COIL TEMP. DROP _________DEG.F
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK OPERATING PRESSURES
RTU | ROOFTOP UNIT | SPRING | #1 DISCH______SUC______#2 DISCH______SUC______
RTU | ROOFTOP UNIT | SPRING | #3 DISCH______SUC______#4 DISCH______SUC______
RTU | ROOFTOP UNIT | SPRING | [ ] CK COMPRESSOR DISCHARGE TEMP #1____#2____#3____#4____
RTU | ROOFTOP UNIT | SPRING | [ ] CK COMPRESSOR SUCTION TEMP #1____#2____#3____#4____
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SUB COOLING #1____#2____#3____#4____
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK OPERATING CONTROLS PRESSURE SETTING
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RTU | ROOFTOP UNIT | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
RTU | ROOFTOP UNIT | SPRING | [ ] LUBE BLOWER MOTOR
RTU | ROOFTOP UNIT | SPRING | [ ] LUBE DAMPER PIVOT POINTS
RTU | ROOFTOP UNIT | SPRING | [ ] LUBE INLET VANE PIVOT POINTS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT AND BULB
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CAPACITY CONTROLS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SAFETIES
RTU | ROOFTOP UNIT | SPRING | [ ] MEG/OHM MOTORS 10.0 HP OR LARGER
RTU | ROOFTOP UNIT | SPRING | COMP #1______#2______#3______#4______
RTU | ROOFTOP UNIT | SPRING | S/A BLOWER #1_____#2_____#3_____#4_____
RTU | ROOFTOP UNIT | SPRING | R/A BLOWER #1_____#2_____
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK OUTDOOR FAN BLADES/SUPPORTS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK FRESH AIR INTAKE SCREENS
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CONDENSER FAN BLADE CONDITION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK CONDENSER FAN SEQUENCE AND OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK VFD,INLET/DISCHARGE VANE OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
RTU | ROOFTOP UNIT | SPRING | EVAPORATIVE CONDENSER
RTU | ROOFTOP UNIT | SPRING | [ ] FILL SUMP IF REQUIRED
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SUMP CONDITION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SPRAY PUMP OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK AUTO FILL VALVE OPERATION
RTU | ROOFTOP UNIT | SPRING | [ ] CHECK SUMP HEATER
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK BELTS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
RTU | ROOFTOP UNIT | SUMMER | [ ] ADD PAN TABS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK UNUSUAL VIBRATION/NOISE
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK INDOOR/OUTDOOR COIL CONDITION
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK SUPPLY VOLTAGE______,______,______
RTU | ROOFTOP UNIT | SUMMER | [ ] SUPPLY MOTOR AMPS #1____,____,____,____#2___,___,___
RTU | ROOFTOP UNIT | SUMMER | #3____,____,____,____#4___,___,___
RTU | ROOFTOP UNIT | SUMMER | [ ] RETURN MOTOR AMPS #1____,____,____ #2____,____,_____
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK ECONOMIZER OPERATION
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK RELIEF DAMPERS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK CONTROL SET POINTS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK OIL LEVEL
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK INDOOR COIL TEMP DROP ________DEG.F
RTU | ROOFTOP UNIT | SUMMER | [ ] CK COMPRESSOR DISCHARGE TEMP. #1___#2___#3___#4___
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK FRESH AIR INTAKE SCREENS
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
RTU | ROOFTOP UNIT | SUMMER | [ ] CHECK HOT GAS BYPASS OPERATION
RTU | ROOFTOP UNIT | SUMMER | [ ] LUBE INLET VANE PIVOT POINTS
RTU | ROOFTOP UNIT | SUMMER | [ ] LUBE DAMPER PIVOT POINTS
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK BLOWER OPERATION
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK BELT
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK PULLEY WEAR
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK DAMPER OPERATION
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK VOLTAGE________________
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK AMPS____________________
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK TEMPERATURE CONTROL
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
RV | ROOFTOP VENTILATOR | FALL | [ ] CHECK CONTACTOR POINTS
RV | ROOFTOP VENTILATOR | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
RV | ROOFTOP VENTILATOR | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
RV | ROOFTOP VENTILATOR | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK BLOWER OPERATION
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK BELT
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK PULLEY WEAR
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK DAMPER OPERATION
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK VOLTAGE___________________
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK AMPS__________________________
RV | ROOFTOP VENTILATOR | WINTER | [ ] CHECK TEMPERATURE CONTROL
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK BLOWER OPERATION
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK BELT
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK PULLEY WEAR
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK DAMPER OPERATION
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK VOLTAGE__________________
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK AMP______________________
RV | ROOFTOP VENTILATOR | SPRING | [ ] CHECK TEMPERATURE CONTROL
RV | ROOFTOP VENTILATOR | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK BLOWER OPERATION
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK BELT
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK PULLEY WEAR
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK DAMPER OPERATION
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK VOLTAGE________________
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK AMPS___________________
RV | ROOFTOP VENTILATOR | SUMMER | [ ] CHECK TEMPERATURE CONTROL
SBB | STEAM BASEBOARD HEATER | FALL | [ ] CHECK TEMPERATURE CONTROL
SBB | STEAM BASEBOARD HEATER | FALL | [ ] CHECK STEAM VALVE OPERATION
SBB | STEAM BASEBOARD HEATER | FALL | [ ] CHECK STEAM TRAP
SBB | STEAM BASEBOARD HEATER | FALL | [ ] CHECK INTERLOCKS
SBB | STEAM BASEBOARD HEATER | WINTER | [ ] CHECK TEMPERATURE CONTROL
SBB | STEAM BASEBOARD HEATER | WINTER | [ ] CHECK STEAM VALVE OPERATION
SBB | STEAM BASEBOARD HEATER | SPRING | [ ] CHECK TEMPERATURE CONTROL
SBB | STEAM BASEBOARD HEATER | SPRING | [ ] CHECK STEAM VALVE OPERATION
SBB | STEAM BASEBOARD HEATER | SUMMER | [ ] CHECK TEMPERATURE CONTROL
SBB | STEAM BASEBOARD HEATER | SUMMER | [ ] CHECK STEAM VALVE OPERATION
SC | STEAM COIL | FALL | [ ] INSPECT CONDITION OF COIL
SC | STEAM COIL | FALL | [ ] CHECK TEMPERATURE CONTROL
SC | STEAM COIL | FALL | [ ] CHECK STEAM VALVE
SC | STEAM COIL | FALL | [ ] CHECK STEAM CONDENSATE TRAP
SC | STEAM COIL | WINTER | [ ] INSPECT CONDITION OF COIL
SC | STEAM COIL | WINTER | [ ] CHECK TEMPERATURE CONTROL
SC | STEAM COIL | WINTER | [ ] CHECK STEAM VALVE
SC | STEAM COIL | SPRING | [ ] INSPECT CONDITION OF COIL
SC | STEAM COIL | SPRING | [ ] CHECK TEMPERATURE CONTROL
SC | STEAM COIL | SPRING | [ ] CHECK STEAM VALVE
SC | STEAM COIL | SUMMER | [ ] INSPECT CONDITION OF COIL
SC | STEAM COIL | SUMMER | [ ] CHECK TEMPERATURE CONTROL
SC | STEAM COIL | SUMMER | [ ] CHECK STEAM VALVE
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK BELTS
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK PULLEY WEAR
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK OPERATION
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK VOLTAGE___________
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK AMPS_______________
SCF | SMOKE CONTROL FAN | FALL | [ ] INSPECT BLOWER FOR DIRT
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK ELECTRICAL CONNECTION
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK CONTACTOR POINTS
SCF | SMOKE CONTROL FAN | FALL | [ ] MEG OHM MOTOR (10HP OR LARGER)
SCF | SMOKE CONTROL FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SCF | SMOKE CONTROL FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK SPRING ISOLATION
SCF | SMOKE CONTROL FAN | FALL | ELECTROSTATIC CLEANER (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | FALL | [ ] OPERATIONAL CHECK
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK FOR MISSING/BROKEN IONIZER WIRES
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK INSULATORS FOR GREASE BUILD-UP
SCF | SMOKE CONTROL FAN | FALL | [ ] INSPECT COLLECTOR PLATES FOR DAMAGE
SCF | SMOKE CONTROL FAN | FALL | WASH CYCLE
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK SUMP LEVEL
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK DRAIN
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK WASHING CYCLE
SCF | SMOKE CONTROL FAN | FALL | [ ] CHECK SPRAY NOZZLES
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK BELTS
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK PULLEY WEAR
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK OPERATION
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK VOLTAGE_______________
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK AMPS____________________
SCF | SMOKE CONTROL FAN | WINTER | [ ] INSPECT BLOWER FOR DIRT
SCF | SMOKE CONTROL FAN | WINTER | ELECTROSTATIC CLEANER (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | WINTER | [ ] OPERATIONAL CHECK
SCF | SMOKE CONTROL FAN | WINTER | WASH CYCLE (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK SOAP LEVEL
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK DRAIN
SCF | SMOKE CONTROL FAN | WINTER | [ ] CHECK WASHING CYCLE
SCF | SMOKE CONTROL FAN | WINTER | [ ] LUBRICATE BEARINGS (PER MFG SPECS)
SCF | SMOKE CONTROL FAN | SPRING | [ ] LUBRICATE BLOWER (PER MFG SPECS)
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK BELTS
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK PULLEY WEAR
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK OPERATION
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK VOLTAGE_______________
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK AMPS_________________
SCF | SMOKE CONTROL FAN | SPRING | [ ] INSPECT BLOWER FOR DIRT
SCF | SMOKE CONTROL FAN | SPRING | ELECTROSTATIC CLEANER (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | SPRING | [ ] OPERATIONAL CHECK
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK FOR MISSING/BROKEN IONIZER WIRE
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK INSULATORS FOR GREASE BUILD-UP
SCF | SMOKE CONTROL FAN | SPRING | [ ] INSPECT COLLECTOR PLATES FOR DAMAGE
SCF | SMOKE CONTROL FAN | SPRING | WASH CYCLE (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK DRAIN
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK WASHING CYCLE
SCF | SMOKE CONTROL FAN | SPRING | [ ] CHECK SPRAY NOZZLES
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK BELTS
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK PULLEY WEAR
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK OPERATION
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK VOLTAGE___________________
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK AMPS______________________
SCF | SMOKE CONTROL FAN | SUMMER | [ ] INSPECT BLOWER FOR DIRT
SCF | SMOKE CONTROL FAN | SUMMER | ELECTROSTATIC CLEANER (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | SUMMER | [ ] OPERATIONAL CHECK
SCF | SMOKE CONTROL FAN | SUMMER | WASH CYCLE (IF APPLICABLE)
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK SOAP LEVEL
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK DRAIN
SCF | SMOKE CONTROL FAN | SUMMER | [ ] CHECK WASHING CYCLE
SCF | SMOKE CONTROL FAN | SUMMER | [ ] LUBRICATE BEARINGS PER MFG SPECS
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK PUMP FLOAT CONTROL
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK VALVE OPERATION
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK AMPS_______________________
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK VOLTAGE__________________
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
SCP | STEAM CONDENSATE PUMP | FALL | [ ] CHECK CONTACTOR POINTS
SCP | STEAM CONDENSATE PUMP | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
SCP | STEAM CONDENSATE PUMP | WINTER | [ ] CHECK PUMP FLOAT CONTROL
SCP | STEAM CONDENSATE PUMP | WINTER | [ ] CHECK VALVE OPERATION
SCP | STEAM CONDENSATE PUMP | WINTER | [ ] CHECK VOLTAGE_____________________
SCP | STEAM CONDENSATE PUMP | WINTER | [ ] CHECK AMPS_________________________
SCP | STEAM CONDENSATE PUMP | SPRING | [ ] CHECK PUMP FLOAT CONTROL
SCP | STEAM CONDENSATE PUMP | SPRING | [ ] CHECK VALVE OPERATION
SCP | STEAM CONDENSATE PUMP | SPRING | [ ] CHECK VOLTAGE__________________
SCP | STEAM CONDENSATE PUMP | SPRING | [ ] CHECK AMPS______________________
SCP | STEAM CONDENSATE PUMP | SUMMER | [ ] CHECK PUMP FLOAT CONTROL
SCP | STEAM CONDENSATE PUMP | SUMMER | [ ] CHECK VALVE OPERATION
SCP | STEAM CONDENSATE PUMP | SUMMER | [ ] CHECK VOLTAGE_________________
SCP | STEAM CONDENSATE PUMP | SUMMER | [ ] CHECK AMPS_____________________
SDF | SAND FILTER | FALL | [ ] DRAIN FOR WINTER
SDF | SAND FILTER | FALL | [ ] DRAIN PUMP VOLUTE
SDF | SAND FILTER | FALL | [ ] CHECK PIPE HEAT TAPE
SDF | SAND FILTER | FALL | [ ] CHECK FLUSH CYCLE
SDF | SAND FILTER | FALL | [ ] CHECK PUMP OPERATION
SDF | SAND FILTER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SDF | SAND FILTER | FALL | [ ] CHECK FOR WATER LEAKS
SDF | SAND FILTER | FALL | [ ] CHECK VOLTAGE______________________
SDF | SAND FILTER | WINTER | [ ] CHECK FLUSH CYCLE
SDF | SAND FILTER | WINTER | [ ] CHECK PUMP OPERATION
SDF | SAND FILTER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SDF | SAND FILTER | WINTER | [ ] CHECK FOR WATER LEAKS
SDF | SAND FILTER | WINTER | [ ] CHECK VOLTAGE______________________
SDF | SAND FILTER | SPRING | [ ] CHECK FLUSH CYCLE
SDF | SAND FILTER | SPRING | [ ] CHECK PUMP OPERATION
SDF | SAND FILTER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SDF | SAND FILTER | SPRING | [ ] CHECK FOR WATER LEAKS
SDF | SAND FILTER | SPRING | [ ] CHECK VOLTAGE___________________
SDF | SAND FILTER | SPRING | [ ] CHECK PRESSURE SWITCH OPERATION
SDF | SAND FILTER | SPRING | [ ] CHECK CONTACTOR POINTS
SDF | SAND FILTER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
SDF | SAND FILTER | SPRING | [ ] FILL SYSTEM
SDF | SAND FILTER | SPRING | [ ] INSPECT LINKAGE
SDF | SAND FILTER | SPRING | [ ] LUBRICATE MOTOR (PER MFG SPECS)
SDF | SAND FILTER | SUMMER | [ ] CHECK FLUSH CYCLE
SDF | SAND FILTER | SUMMER | [ ] CHECK PUMP OPERATION
SDF | SAND FILTER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SDF | SAND FILTER | SUMMER | [ ] CHECK FOR WATER LEAKS
SDF | SAND FILTER | SUMMER | [ ] CHECK VOLTAGE___________________
SF | SUPPLY FAN | FALL | [ ] CHECK BELTS
SF | SUPPLY FAN | FALL | [ ] CHECK PULLEY ALIGNMENT
SF | SUPPLY FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SF | SUPPLY FAN | FALL | [ ] CHECK PULLEY WEAR
SF | SUPPLY FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SF | SUPPLY FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SF | SUPPLY FAN | FALL | DUCT HEATER
SF | SUPPLY FAN | FALL | [ ] CHECK SEQUENCE OF OPERATION
SF | SUPPLY FAN | FALL | [ ] CHECK VOLTAGE_______,_______,_______
SF | SUPPLY FAN | FALL | [ ] CHECK AMPS_______,_______,_______
SF | SUPPLY FAN | FALL | [ ] CHECK TEMPERATURE____________DEG F.
SF | SUPPLY FAN | FALL | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SF | SUPPLY FAN | WINTER | [ ] CHECK BELTS
SF | SUPPLY FAN | WINTER | [ ] CHECK PULLEY ALIGNMENT
SF | SUPPLY FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SF | SUPPLY FAN | WINTER | [ ] CHECK PULLEY WEAR
SF | SUPPLY FAN | WINTER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SF | SUPPLY FAN | WINTER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SF | SUPPLY FAN | WINTER | DUCT HEATER
SF | SUPPLY FAN | WINTER | [ ] CHECK SEQUENCE OF OPERATION
SF | SUPPLY FAN | WINTER | [ ] CHECK DISCHARGE TEMPERATURE ________DEG F.
SF | SUPPLY FAN | WINTER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SF | SUPPLY FAN | SPRING | [ ] CHECK BELTS
SF | SUPPLY FAN | SPRING | [ ] CHECK PULLEY ALIGNMENT
SF | SUPPLY FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SF | SUPPLY FAN | SPRING | [ ] CHECK PULLEY WEAR
SF | SUPPLY FAN | SPRING | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SF | SUPPLY FAN | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SF | SUPPLY FAN | SPRING | ON ALL THREE PHASE MOTORS
SF | SUPPLY FAN | SPRING | [ ] CHECK AMPS L1_____L2_____L3_____
SF | SUPPLY FAN | SPRING | [ ] CHECK VOLTAGE L1_____L2_____L3_____
SF | SUPPLY FAN | SPRING | [ ] CHECK CONTACTOR/STARTER POINTS
SF | SUPPLY FAN | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
SF | SUPPLY FAN | SPRING | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SF | SUPPLY FAN | SUMMER | [ ] CHECK BELTS
SF | SUPPLY FAN | SUMMER | [ ] CHECK PULLEY ALIGNMENT
SF | SUPPLY FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SF | SUPPLY FAN | SUMMER | [ ] CHECK PULLEY WEAR
SF | SUPPLY FAN | SUMMER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SF | SUPPLY FAN | SUMMER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SF | SUPPLY FAN | SUMMER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SLCH | SCROLL CHILLER | FALL | [ ] CHECK COMPRESSOR OIL LEVELS
SLCH | SCROLL CHILLER | FALL | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SLCH | SCROLL CHILLER | FALL | LOAD CONDITION:
SLCH | SCROLL CHILLER | FALL | A. DISCHARGE LINE TEMPERATURE:
SLCH | SCROLL CHILLER | FALL | COMP #1 ________DEG.F COMP #2 ________DEG.F
SLCH | SCROLL CHILLER | FALL | COMP #3 ________DEG.F COMP #4 ________DEG.F
SLCH | SCROLL CHILLER | FALL | B. OUTSIDE AIR TEMP: ________DEG.F
SLCH | SCROLL CHILLER | FALL | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | FALL | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | FALL | [ ] CHECK OUTDOOR COIL CONDITION
SLCH | SCROLL CHILLER | FALL | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
SLCH | SCROLL CHILLER | FALL | [ ] CHECK HOT GAS BY-PASS OPERATION
SLCH | SCROLL CHILLER | FALL | [ ] CHECK CRANKCASE HEATERS
SLCH | SCROLL CHILLER | FALL | [ ] CHANGE LEAD COMPRESSOR
SLCH | SCROLL CHILLER | FALL | [ ] CHECK SEQUENCE OF OPERATION
SLCH | SCROLL CHILLER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASSES
SLCH | SCROLL CHILLER | FALL | [ ] CHECK CONTROL SETPOINTS
SLCH | SCROLL CHILLER | FALL | [ ] CHECK ALL MOTORS AMPS
SLCH | SCROLL CHILLER | FALL | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SLCH | SCROLL CHILLER | FALL | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SLCH | SCROLL CHILLER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SLCH | SCROLL CHILLER | FALL | [ ] CHECK CAPACITY CONTROLS
SLCH | SCROLL CHILLER | FALL | [ ] CHECK SAFETY CONTROLS
SLCH | SCROLL CHILLER | FALL | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
SLCH | SCROLL CHILLER | FALL | OUTLET________PSI
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK COMPRESSOR OIL LEVELS:
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SLCH | SCROLL CHILLER | WINTER | LOAD CONDITION:
SLCH | SCROLL CHILLER | WINTER | A. DISCHARGE LINE TEMP:
SLCH | SCROLL CHILLER | WINTER | COMP #1 ________DEG.F COMP #2 ________DEG.F
SLCH | SCROLL CHILLER | WINTER | COMP #3 ________DEG.F COMP #4 ________DEG.F
SLCH | SCROLL CHILLER | WINTER | B. OUTSIDE AIR TEMP: _________DEG.F
SLCH | SCROLL CHILLER | WINTER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | WINTER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK OUTDOOR COIL CONDITION
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK CRANKCASE HEATERS
SLCH | SCROLL CHILLER | WINTER | [ ] CHANGE LEAD COMPRESSOR
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASSES
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK CONTROL SET POINTS
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK ALL MOTORS AMPS
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SLCH | SCROLL CHILLER | WINTER | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
SLCH | SCROLL CHILLER | WINTER | OUTLET________PSI
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK COMPRESSOR OIL LEVELS:
SLCH | SCROLL CHILLER | SPRING | [ ] OIL SAMPLE #1_____#2_____#3_____#4_____
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SLCH | SCROLL CHILLER | SPRING | LOAD CONDITION:
SLCH | SCROLL CHILLER | SPRING | A. DISCHARGE PRESSURE:
SLCH | SCROLL CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SLCH | SCROLL CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SLCH | SCROLL CHILLER | SPRING | B. SUCTION PRESSURE:
SLCH | SCROLL CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SLCH | SCROLL CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SLCH | SCROLL CHILLER | SPRING | C. NET OIL PRESSURE:
SLCH | SCROLL CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SLCH | SCROLL CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SLCH | SCROLL CHILLER | SPRING | D. CIRCUIT SUPERHEAT:
SLCH | SCROLL CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | E. SYSTEM SUBCOOLING:
SLCH | SCROLL CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | F. DISCHARGE LINE TEMPERATURE:
SLCH | SCROLL CHILLER | SPRING | COMP #1 ________DEG.F COMP #2 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | COMP #3 ________DEG.F COMP #4 ________DEG.F
SLCH | SCROLL CHILLER | SPRING | G. OUTSIDE AIR TEMP: ________DEG.F
SLCH | SCROLL CHILLER | SPRING | H. CHILLED WTR TEMP: IN________DEG.F
SLCH | SCROLL CHILLER | SPRING | OUT________DEG.F
SLCH | SCROLL CHILLER | SPRING | I. CONDENSER WATER TEMP: IN________DEG.F
SLCH | SCROLL CHILLER | SPRING | OUT________DEG.F
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK OUTDOOR COIL CONDITION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK OUTDOOR FANS CONDITION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK OUTDOOR FAN MOTORS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK TXV SENSING BULBS FOR CLEANLINESS & CONTACT
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK CRANKCASE HEATERS
SLCH | SCROLL CHILLER | SPRING | [ ] CHANGE LEAD COMPRESSOR
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK SEQUENCE OF OPERATION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASSES
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK CONTROL SET POINTS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK ALL MOTORS AMPS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK CAPACITY CONTROLS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK SAFETY CONTROLS
SLCH | SCROLL CHILLER | SPRING | FREEZE PROTECTION____________
SLCH | SCROLL CHILLER | SPRING | OIL FAILURE_____________
SLCH | SCROLL CHILLER | SPRING | LOW AND HIGH PRESSURE_____________
SLCH | SCROLL CHILLER | SPRING | FLOW SWITCH__________________
SLCH | SCROLL CHILLER | SPRING | [ ] MEG OHM MOTOR 10 HP OR LARGER
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK CONTACTOR POINTS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK CHILLED WTR PRESS: IN________PSI
SLCH | SCROLL CHILLER | SPRING | OUT________PSI
SLCH | SCROLL CHILLER | SPRING | [ ] INSPECT RELIEF VALVE
SLCH | SCROLL CHILLER | SPRING | [ ] CHANGE MOTOR COOLER REFRIGERANT DRIER (IF REQ)
SLCH | SCROLL CHILLER | SPRING | [ ] CHANGE OIL STRAINER / OIL RETURN SYSTEM (IF REQ)
SLCH | SCROLL CHILLER | SPRING | [ ] INSPECT FLOAT VALVE ASSEMBLY (IF REQ)
SLCH | SCROLL CHILLER | SPRING | [ ] CHECK STARTER OVERLOADS AND TIME DELAYS
SLCH | SCROLL CHILLER | SPRING | [ ] RECORD INFORMATION IN CUSTOMERS LOG
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK COMPRESSOR OIL LEVELS:
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SLCH | SCROLL CHILLER | SUMMER | LOAD CONDITION:
SLCH | SCROLL CHILLER | SUMMER | A. DISCHARGE LINE TEMPERATURE:
SLCH | SCROLL CHILLER | SUMMER | COMP #1 ________DEG.F COMP #2 ________DEG.F
SLCH | SCROLL CHILLER | SUMMER | COMP #3 ________DEG.F COMP #4 ________DEG.F
SLCH | SCROLL CHILLER | SUMMER | B. OUTSIDE AIR TEMP: ________DEG.F
SLCH | SCROLL CHILLER | SUMMER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | SUMMER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK OUTDOOR COIL CONDITION
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK CRANKCASE HEATERS
SLCH | SCROLL CHILLER | SUMMER | [ ] CHANGE LEAD COMPRESSOR
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASSES
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK CONTROL SET POINTS
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK ALL MOTORS AMPS
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK SAFETY CONTROLS
SLCH | SCROLL CHILLER | SUMMER | [ ] CHECK CHILLED WTR PRESS. IN________PSI
SLCH | SCROLL CHILLER | SUMMER | OUT________PSI
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK FLOAT OPERATION
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK PUMP ALTERNATOR OPERATION
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK PUMP ALARMS
SLP | SEWAGE LIFT PUMP | FALL | [ ] INSPECT PUMP COUPLINGS
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK ELECTRICAL CONNECTION
SLP | SEWAGE LIFT PUMP | FALL | [ ] CHECK CONTACTOR POINTS
SLP | SEWAGE LIFT PUMP | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
SLP | SEWAGE LIFT PUMP | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
SLP | SEWAGE LIFT PUMP | FALL | [ ] LUBRICATE SHAFT BEARINGS (PER MFG SPECS)
SLP | SEWAGE LIFT PUMP | FALL | [ ] INSPECT PIT FOR SLUDGE BUILD UP
SLP | SEWAGE LIFT PUMP | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SLP | SEWAGE LIFT PUMP | WINTER | [ ] CHECK FLOAT OPERATION
SLP | SEWAGE LIFT PUMP | WINTER | [ ] CHECK PUMP ALTERNATOR OPERATION
SLP | SEWAGE LIFT PUMP | WINTER | [ ] CHECK PUMP ALARMS
SLP | SEWAGE LIFT PUMP | WINTER | [ ] INSPECT PUMP COUPLING
SLP | SEWAGE LIFT PUMP | SPRING | [ ] LUBRICATE SHAFT BEARINGS (PER MFG SPECS)
SLP | SEWAGE LIFT PUMP | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
SLP | SEWAGE LIFT PUMP | SPRING | [ ] CHECK FLOAT OPERATION
SLP | SEWAGE LIFT PUMP | SPRING | [ ] CHECK PUMP ALTERNATOR OPERATION
SLP | SEWAGE LIFT PUMP | SPRING | [ ] CHECK PUMP ALARMS
SLP | SEWAGE LIFT PUMP | SPRING | [ ] INSPECT PUMP COUPLING
SLP | SEWAGE LIFT PUMP | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
SLP | SEWAGE LIFT PUMP | SUMMER | [ ] CHECK FLOAT OPERATION
SLP | SEWAGE LIFT PUMP | SUMMER | [ ] CHECK PUMP ALTERNATOR OPERATION
SLP | SEWAGE LIFT PUMP | SUMMER | [ ] CHECK PUMP ALARMS
SLP | SEWAGE LIFT PUMP | SUMMER | [ ] INSPECT PUMP COUPLING
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CLEAN AIR FILTER
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CABINET HOUSING
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK FOR LOOSE ASSEMBLY AND MAKE SURE ALL
SPC | SPOT COOLER-PORTABLE | FALL | CABINET COMPONENTS ARE INTACT
SPC | SPOT COOLER-PORTABLE | FALL | [ ] VISUAL CHECK FOR LOOSE OR DISCOLORED WIRES,
SPC | SPOT COOLER-PORTABLE | FALL | TIGHTEN ONE TIME PER YEAR
SPC | SPOT COOLER-PORTABLE | FALL | [ ] EVAPORATOR MOTOR
SPC | SPOT COOLER-PORTABLE | FALL | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | FALL | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CONDENSER MOTOR
SPC | SPOT COOLER-PORTABLE | FALL | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | FALL | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | FALL | [ ] COMPRESSOR AND REFRIGERATION SYSTEM
SPC | SPOT COOLER-PORTABLE | FALL | [ ] COMPRESSOR RATED AMPS_______ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | FALL | [ ] AIR "IN" TEMPERATURE___________________
SPC | SPOT COOLER-PORTABLE | FALL | [ ] AIR "OUT" TEMPERATURE
SPC | SPOT COOLER-PORTABLE | FALL | [ ] TEMPERATURE DIFFERENTIAL____________
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK DISCHARGE LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK SUCTION LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | FALL | [ ] COILS
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK AND CLEAN COILS AND DRAIN PAN
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CONDENSATE PUMP
SPC | SPOT COOLER-PORTABLE | FALL | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CLEAN PAN BENEATH CONDENSATE PUMP WHEN MINERAL
SPC | SPOT COOLER-PORTABLE | FALL | DEPOSITS ARE VISIBLE
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CONDENSATE TANK
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK CUT-OFF SWITCH OPERATION AND CLEAN
SPC | SPOT COOLER-PORTABLE | FALL | AS NEEDED
SPC | SPOT COOLER-PORTABLE | FALL | [ ] ELECTRICAL SYSTEMS
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK THERMOSTAT OPERATION
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CONTROL SWITCH (ROCKER) OPERATION
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK FAN SPEED SWITCH
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK HIGH PRESSURE SWITCH OPERATION
SPC | SPOT COOLER-PORTABLE | FALL | [ ] CHECK VOLTAGE
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CLEAN AIR FILTER
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CABINET HOUSING
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK FOR LOOSE ASSEMBLY AND MAKE SURE ALL
SPC | SPOT COOLER-PORTABLE | WINTER | CABINET COMPONENTS ARE INTACT
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] VISUAL CHECK FOR LOOSE OR DISCOLORED WIRES,
SPC | SPOT COOLER-PORTABLE | WINTER | TIGHTEN ONE TIME PER YEAR
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] EVAPORATOR MOTOR
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CONDENSER MOTOR
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] COMPRESSOR AND REFRIGERATION SYSTEM
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] COMPRESSOR RATED AMPS_______ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] AIR "IN" TEMPERATURE___________________
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] AIR "OUT" TEMPERATURE
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] TEMPERATURE DIFFERENTIAL____________
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK DISCHARGE LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK SUCTION LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] COILS
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK AND CLEAN COILS AND DRAIN PAN
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CONDENSATE PUMP
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CLEAN PAN BENEATH CONDENSATE PUMP WHEN MINERAL
SPC | SPOT COOLER-PORTABLE | WINTER | DEPOSITS ARE VISIBLE
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CONDENSATE TANK
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK CUT-OFF SWITCH OPERATION AND CLEAN
SPC | SPOT COOLER-PORTABLE | WINTER | AS NEEDED
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] ELECTRICAL SYSTEMS
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK THERMOSTAT OPERATION
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CONTROL SWITCH (ROCKER) OPERATION
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK FAN SPEED SWITCH
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK HIGH PRESSURE SWITCH OPERATION
SPC | SPOT COOLER-PORTABLE | WINTER | [ ] CHECK VOLTAGE
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CLEAN AIR FILTER
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CABINET HOUSING
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK FOR LOOSE ASSEMBLY AND MAKE SURE ALL
SPC | SPOT COOLER-PORTABLE | SPRING | CABINET COMPONENTS ARE INTACT
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] VISUAL CHECK FOR LOOSE OR DISCOLORED WIRES,
SPC | SPOT COOLER-PORTABLE | SPRING | TIGHTEN ONE TIME PER YEAR
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] EVAPORATOR MOTOR
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CONDENSER MOTOR
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] COMPRESSOR AND REFRIGERATION SYSTEM
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] COMPRESSOR RATED AMPS_______ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] AIR "IN" TEMPERATURE___________________
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] AIR "OUT" TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] TEMPERATURE DIFFERENTIAL____________
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK DISCHARGE LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK SUCTION LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] COILS
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK AND CLEAN COILS AND DRAIN PAN
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CONDENSATE PUMP
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CLEAN PAN BENEATH CONDENSATE PUMP WHEN MINERAL
SPC | SPOT COOLER-PORTABLE | SPRING | DEPOSITS ARE VISIBLE
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CONDENSATE TANK
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK CUT-OFF SWITCH OPERATION AND CLEAN
SPC | SPOT COOLER-PORTABLE | SPRING | AS NEEDED
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] ELECTRICAL SYSTEMS
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK THERMOSTAT OPERATION
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CONTROL SWITCH (ROCKER) OPERATION
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK FAN SPEED SWITCH
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK HIGH PRESSURE SWITCH OPERATION
SPC | SPOT COOLER-PORTABLE | SPRING | [ ] CHECK VOLTAGE
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CLEAN AIR FILTER
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CABINET HOUSING
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK FOR LOOSE ASSEMBLY AND MAKE SURE ALL
SPC | SPOT COOLER-PORTABLE | SUMMER | CABINET COMPONENTS ARE INTACT
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] VISUAL CHECK FOR LOOSE OR DISCOLORED WIRES,
SPC | SPOT COOLER-PORTABLE | SUMMER | TIGHTEN ONE TIME PER YEAR
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] EVAPORATOR MOTOR
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CONDENSER MOTOR
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] RATED AMPS_________ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK ROTATION AND ALIGNMENT
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] COMPRESSOR AND REFRIGERATION SYSTEM
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] COMPRESSOR RATED AMPS_______ACTUAL AMPS________
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] AIR "IN" TEMPERATURE___________________
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] AIR "OUT" TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] TEMPERATURE DIFFERENTIAL____________
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK DISCHARGE LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK SUCTION LINE TEMPERATURE
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] COILS
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK AND CLEAN COILS AND DRAIN PAN
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CONDENSATE PUMP
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] ADD OIL PER MANUFACTURER RECOMMENDATIONS
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CLEAN PAN BENEATH CONDENSATE PUMP WHEN MINERAL
SPC | SPOT COOLER-PORTABLE | SUMMER | DEPOSITS ARE VISIBLE
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CONDENSATE TANK
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK CUT-OFF SWITCH OPERATION AND CLEAN
SPC | SPOT COOLER-PORTABLE | SUMMER | AS NEEDED
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] ELECTRICAL SYSTEMS
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK THERMOSTAT OPERATION
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CONTROL SWITCH (ROCKER) OPERATION
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK FAN SPEED SWITCH
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK HIGH PRESSURE SWITCH OPERATION
SPC | SPOT COOLER-PORTABLE | SUMMER | [ ] CHECK VOLTAGE
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK BELTS
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK PULLEY ALIGNMENT
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK PULLEY WEAR
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | FALL | DUCT HEATER
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK SEQUENCE OF OPERATION
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK VOLTAGE_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK AMPS_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK TEMPERATURE____________DEG F.
SPF | STAIRWELL PRESSURIZATION FAN | FALL | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK BELTS
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK PULLEY ALIGNMENT
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK PULLEY WEAR
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | DUCT HEATER
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK SEQUENCE OF OPERATION
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK VOLTAGE_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK AMPS_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK TEMPERATURE____________DEG F.
SPF | STAIRWELL PRESSURIZATION FAN | WINTER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK BELTS
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK PULLEY ALIGNMENT
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK PULLEY WEAR
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | DUCT HEATER
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK SEQUENCE OF OPERATION
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK VOLTAGE_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK AMPS_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK TEMPERATURE____________DEG F.
SPF | STAIRWELL PRESSURIZATION FAN | SPRING | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK BELTS
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK PULLEY ALIGNMENT
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK PULLEY WEAR
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] LUBRICATE BLOWER MOTOR (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | DUCT HEATER
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK VOLTAGE_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK AMPS_______,_______,_______
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK TEMPERATURE____________DEG F.
SPF | STAIRWELL PRESSURIZATION FAN | SUMMER | [ ] CHECK AND CLEAN FRESH AIR SCREENS IF NEEDED
SR | STEAM RADIATOR | FALL | [ ] CHECK TEMPERATURE CONTROL
SR | STEAM RADIATOR | FALL | [ ] CHECK STEAM VALVE OPERATION
SR | STEAM RADIATOR | FALL | [ ] CHECK STEAM TRAP
SR | STEAM RADIATOR | WINTER | [ ] CHECK TEMPERATURE CONTROL
SR | STEAM RADIATOR | WINTER | [ ] CHECK STEAM VALVE OPERATION
SR | STEAM RADIATOR | SPRING | [ ] CHECK TEMPERATURE CONTROL
SR | STEAM RADIATOR | SPRING | [ ] CHECK STEAM VALVE OPERATION
SR | STEAM RADIATOR | SUMMER | [ ] CHECK TEMPERATURE CONTROL
SR | STEAM RADIATOR | SUMMER | [ ] CHECK STEAM VALVE OPERATION
SRS | SMOKE REMOVAL SYSTEM | FALL | MONTHLY
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] EXCHANGE 3 DIRTIEST ELECTROSTATIC CELLS
SRS | SMOKE REMOVAL SYSTEM | FALL | 2 INSIDE AND 1 OUTSIDE
SRS | SMOKE REMOVAL SYSTEM | FALL | WITH CUSTOMER PROVIDED SPARE CELLS TO PROVIDE
SRS | SMOKE REMOVAL SYSTEM | FALL | AN ONGOING ROTATION OF CLEAN CELLS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] CHANGE OUT 9 DEBRIS SCREENS WITH CLEAN SCREENS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] SCRAPE OUT ELECTROSTATIC CELL TRACKS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] SCRAPE OUT BASE OF UNIT - CHECK FOR PROPER DRAINAGE
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] CHECK FOR BROKEN IONIZATION WIRES
SRS | SMOKE REMOVAL SYSTEM | FALL
SRS | SMOKE REMOVAL SYSTEM | FALL | QUARTERLY
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] REFILL 72 PM-18 ODOR CONTROL MODULES WITH POTASSIUM
SRS | SMOKE REMOVAL SYSTEM | FALL | PERMANGANATE/ACTIVATED ALUMINA GRANUALS
SRS | SMOKE REMOVAL SYSTEM | FALL | (PURAFILL EQUIVALENT)
SRS | SMOKE REMOVAL SYSTEM | FALL | 2,160 LBS PER CHANGE. DISPOSE OF SPENT GRANULE MEDIA
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] REPLACE PRE FILTERS AND DISPOSE OF DIRY FILTERS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] CHECK FAN BELTS AND MOTOR SHEAVES FOR ALIGNMENT/WEAR
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] LUBRICATE MOTOR AND FAN SHAFTS AS REQUIRED.
SRS | SMOKE REMOVAL SYSTEM | FALL
SRS | SMOKE REMOVAL SYSTEM | FALL | SEMI-ANNUALLY
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] REPLACE FINAL FILTERS AND AFTER FILTERS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] DISPOSE OF DIRTY FILTERS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR TIGHTNESS
SRS | SMOKE REMOVAL SYSTEM | FALL | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR LEAKS
SRS | SMOKE REMOVAL SYSTEM | WINTER | MONTHLY
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] EXCHANGE 3 DIRTIEST ELECTROSTATIC CELLS
SRS | SMOKE REMOVAL SYSTEM | WINTER | 2 INSIDE AND 1 OUTSIDE
SRS | SMOKE REMOVAL SYSTEM | WINTER | WITH CUSTOMER PROVIDED SPARE CELLS TO PROVIDE
SRS | SMOKE REMOVAL SYSTEM | WINTER | AN ONGOING ROTATION OF CLEAN CELLS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] CHANGE OUT 9 DEBRIS SCREENS WITH CLEAN SCREENS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] SCRAPE OUT ELECTROSTATIC CELL TRACKS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] SCRAPE OUT BASE OF UNIT - CHECK FOR PROPER DRAINAGE
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] CHECK FOR BROKEN IONIZATION WIRES
SRS | SMOKE REMOVAL SYSTEM | WINTER
SRS | SMOKE REMOVAL SYSTEM | WINTER | QUARTERLY
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] REFILL 72 PM-18 ODOR CONTROL MODULES WITH POTASSIUM
SRS | SMOKE REMOVAL SYSTEM | WINTER | PERMANGANATE/ACTIVATED ALUMINA GRANUALS
SRS | SMOKE REMOVAL SYSTEM | WINTER | (PURAFILL EQUIVALENT)
SRS | SMOKE REMOVAL SYSTEM | WINTER | 2,160 LBS PER CHANGE. DISPOSE OF SPENT GRANULE MEDIA
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] REPLACE PRE FILTERS AND DISPOSE OF DIRY FILTERS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] CHECK FAN BELTS AND MOTOR SHEAVES FOR ALIGNMENT/WEAR
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] LUBRICATE MOTOR AND FAN SHAFTS AS REQUIRED.
SRS | SMOKE REMOVAL SYSTEM | WINTER
SRS | SMOKE REMOVAL SYSTEM | WINTER | SEMI-ANNUALLY
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] REPLACE FINAL FILTERS AND AFTER FILTERS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] DISPOSE OF DIRTY FILTERS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR TIGHTNESS
SRS | SMOKE REMOVAL SYSTEM | WINTER | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR LEAKS
SRS | SMOKE REMOVAL SYSTEM | SPRING | MONTHLY
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] EXCHANGE 3 DIRTIEST ELECTROSTATIC CELLS
SRS | SMOKE REMOVAL SYSTEM | SPRING | 2 INSIDE AND 1 OUTSIDE
SRS | SMOKE REMOVAL SYSTEM | SPRING | WITH CUSTOMER PROVIDED SPARE CELLS TO PROVIDE
SRS | SMOKE REMOVAL SYSTEM | SPRING | AN ONGOING ROTATION OF CLEAN CELLS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] CHANGE OUT 9 DEBRIS SCREENS WITH CLEAN SCREENS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] SCRAPE OUT ELECTROSTATIC CELL TRACKS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] SCRAPE OUT BASE OF UNIT - CHECK FOR PROPER DRAINAGE
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] CHECK FOR BROKEN IONIZATION WIRES
SRS | SMOKE REMOVAL SYSTEM | SPRING
SRS | SMOKE REMOVAL SYSTEM | SPRING | QUARTERLY
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] REFILL 72 PM-18 ODOR CONTROL MODULES WITH POTASSIUM
SRS | SMOKE REMOVAL SYSTEM | SPRING | PERMANGANATE/ACTIVATED ALUMINA GRANUALS
SRS | SMOKE REMOVAL SYSTEM | SPRING | (PURAFILL EQUIVALENT)
SRS | SMOKE REMOVAL SYSTEM | SPRING | 2,160 LBS PER CHANGE. DISPOSE OF SPENT GRANULE MEDIA
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] REPLACE PRE FILTERS AND DISPOSE OF DIRY FILTERS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] CHECK FAN BELTS AND MOTOR SHEAVES FOR ALIGNMENT/WEAR
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] LUBRICATE MOTOR AND FAN SHAFTS AS REQUIRED.
SRS | SMOKE REMOVAL SYSTEM | SPRING
SRS | SMOKE REMOVAL SYSTEM | SPRING | SEMI-ANNUALLY
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] REPLACE FINAL FILTERS AND AFTER FILTERS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] DISPOSE OF DIRTY FILTERS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR TIGHTNESS
SRS | SMOKE REMOVAL SYSTEM | SPRING | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR LEAKS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | MONTHLY
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] EXCHANGE 3 DIRTIEST ELECTROSTATIC CELLS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | 2 INSIDE AND 1 OUTSIDE
SRS | SMOKE REMOVAL SYSTEM | SUMMER | WITH CUSTOMER PROVIDED SPARE CELLS TO PROVIDE
SRS | SMOKE REMOVAL SYSTEM | SUMMER | AN ONGOING ROTATION OF CLEAN CELLS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] CHANGE OUT 9 DEBRIS SCREENS WITH CLEAN SCREENS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] SCRAPE OUT ELECTROSTATIC CELL TRACKS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] SCRAPE OUT BASE OF UNIT - CHECK FOR PROPER DRAINAGE
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] CHECK FOR BROKEN IONIZATION WIRES
SRS | SMOKE REMOVAL SYSTEM | SUMMER
SRS | SMOKE REMOVAL SYSTEM | SUMMER | QUARTERLY
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] REFILL 72 PM-18 ODOR CONTROL MODULES WITH POTASSIUM
SRS | SMOKE REMOVAL SYSTEM | SUMMER | PERMANGANATE/ACTIVATED ALUMINA GRANUALS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | (PURAFILL EQUIVALENT)
SRS | SMOKE REMOVAL SYSTEM | SUMMER | 2,160 LBS PER CHANGE. DISPOSE OF SPENT GRANULE MEDIA
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] REPLACE PRE FILTERS AND DISPOSE OF DIRY FILTERS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] CHECK FAN BELTS AND MOTOR SHEAVES FOR ALIGNMENT/WEAR
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] LUBRICATE MOTOR AND FAN SHAFTS AS REQUIRED.
SRS | SMOKE REMOVAL SYSTEM | SUMMER
SRS | SMOKE REMOVAL SYSTEM | SUMMER | SEMI-ANNUALLY
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] REPLACE FINAL FILTERS AND AFTER FILTERS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] DISPOSE OF DIRTY FILTERS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR TIGHTNESS
SRS | SMOKE REMOVAL SYSTEM | SUMMER | [ ] CHECK DETERGENT PUMP SYSTEM FITTINGS FOR LEAKS
ST | STORAGE TANK | FALL | [ ] CHECK FOR WATER LEAKS
ST | STORAGE TANK | FALL | [ ] CHECK TANK PRESSURE
ST | STORAGE TANK | FALL | [ ] CHECK TEMPERATURE
ST | STORAGE TANK | WINTER | [ ] CHECK FOR WATER LEAKS
ST | STORAGE TANK | WINTER | [ ] CHECK TANK PRESSURE
ST | STORAGE TANK | WINTER | [ ] CHECK TEMPERATURE
ST | STORAGE TANK | SPRING | [ ] CHECK FOR WATER LEAKS
ST | STORAGE TANK | SPRING | [ ] CHECK TANK PRESSURE
ST | STORAGE TANK | SPRING | [ ] CHECK TEMPERATURE
ST | STORAGE TANK | SUMMER | [ ] CHECK FOR WATER LEAKS
ST | STORAGE TANK | SUMMER | [ ] CHECK TANK PRESSURE
ST | STORAGE TANK | SUMMER | [ ] CHECK TEMPERATURE
STR | STEAM TRAP | FALL | [ ] CHECK TEMPERATURE DIFFERENTIAL
STR | STEAM TRAP | FALL | [ ] VISUAL CHECK FOR STEAM OR CONDENSATE LEAKS
STR | STEAM TRAP | WINTER | [ ] VISUALLY CHECK FOR STEAM OR CONDENSATE LEAKS
STR | STEAM TRAP | WINTER | [ ] CHECK TEMPERATURE DIFFERENTIAL
STR | STEAM TRAP | SPRING | [ ] VISUALLY CHECK FOR STEAM AND CONDENSATE LEAKS
STR | STEAM TRAP | SPRING | [ ] CHECK TEMPERATURE DIFFERENTIAL
STR | STEAM TRAP | SUMMER | [ ] VISUALLY CHECK FOR STEAM AND CONDENSATE LEAKS
STR | STEAM TRAP | SUMMER | [ ] CHECK TEMPERATURE DIFFERENTIAL
SWC | SWAMP COOLER | FALL | [ ] CHECK HEAT OPERATION IF EQUIPPED
SWC | SWAMP COOLER | FALL | [ ] CHECK DISCHARGE TEMPERATURE IF EQUIPPED
SWC | SWAMP COOLER | FALL | [ ] DISABLE SPRAY PUMP
SWC | SWAMP COOLER | FALL | [ ] SECURE MAKE UP WATER LINE
SWC | SWAMP COOLER | FALL | [ ] CHECK MAKE UP WATER PIPE FREEZE PROTECTION OR DRAIN
SWC | SWAMP COOLER | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SWC | SWAMP COOLER | FALL | [ ] DRAIN SUMP
SWC | SWAMP COOLER | FALL | [ ] CLEAN SUMP
SWC | SWAMP COOLER | FALL | [ ] CHECK FLOAT VALVE
SWC | SWAMP COOLER | FALL | [ ] CHECK BLOWER BELT
SWC | SWAMP COOLER | FALL | [ ] CHECK BEARINGS FOR WEAR
SWC | SWAMP COOLER | FALL | [ ] INSPECT EVAPORATION MATS
SWC | SWAMP COOLER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SWC | SWAMP COOLER | FALL | [ ] CHECK SPRAY PUMP AND DISTRIBUTION SYSTEM
SWC | SWAMP COOLER | FALL | [ ] CHECK VOLTAGE_______________
SWC | SWAMP COOLER | FALL | [ ] CHECK AMPS___________________
SWC | SWAMP COOLER | WINTER | [ ] CHECK FLOAT VALVE
SWC | SWAMP COOLER | WINTER | [ ] CHECK BLOWER BELT
SWC | SWAMP COOLER | WINTER | [ ] CHECK BEARING FOR WEAR
SWC | SWAMP COOLER | WINTER | [ ] INSPECT EVAPORATION MATS
SWC | SWAMP COOLER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SWC | SWAMP COOLER | WINTER | [ ] CHECK SPRAY PUMP AND DISTRIBUTION SYSTEM
SWC | SWAMP COOLER | WINTER | [ ] CHECK VOLTAGE________________
SWC | SWAMP COOLER | WINTER | [ ] CHECK AMPS______________
SWC | SWAMP COOLER | SPRING | [ ] CHECK FLOAT VALVE
SWC | SWAMP COOLER | SPRING | [ ] CHECK BLOWER BELT
SWC | SWAMP COOLER | SPRING | [ ] CHECK BEARINGS FOR WEAR
SWC | SWAMP COOLER | SPRING | [ ] INSPECT EVAPORATION MATS
SWC | SWAMP COOLER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SWC | SWAMP COOLER | SPRING | [ ] CHECK SPRAY PUMP AND DISTRIBUTION SYSTEM
SWC | SWAMP COOLER | SPRING | [ ] CHECK VOLTAGE___________________
SWC | SWAMP COOLER | SPRING | [ ] CHECK AMPS_____________________
SWC | SWAMP COOLER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
SWC | SWAMP COOLER | SPRING | [ ] CHECK CONTACTOR POINTS
SWC | SWAMP COOLER | SPRING | [ ] MEG OHM MOTOR (10 HP OR LARGER)
SWC | SWAMP COOLER | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
SWC | SWAMP COOLER | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
SWC | SWAMP COOLER | SPRING | [ ] INSPECT FOR DIRTY BLOWER WHEEL
SWC | SWAMP COOLER | SPRING | [ ] INSPECT FOR CORROSION IN PAN
SWC | SWAMP COOLER | SPRING | [ ] FILL SUMP WITH WATER
SWC | SWAMP COOLER | SUMMER | [ ] CHECK FLOAT VALVE
SWC | SWAMP COOLER | SUMMER | [ ] CHECK BLOWER BELT
SWC | SWAMP COOLER | SUMMER | [ ] CHECK BEARINGS FOR WEAR
SWC | SWAMP COOLER | SUMMER | [ ] INSPECT EVAPORATION MATS
SWC | SWAMP COOLER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
SWC | SWAMP COOLER | SUMMER | [ ] CHECK SPRAY PUMP AND DISTRIBUTION SYSTEM
SWC | SWAMP COOLER | SUMMER | [ ] CHECK VOLTAGE___________________
SWC | SWAMP COOLER | SUMMER | [ ] CHECK AMPS______________________
SWCH | SCREW CHILLER | FALL | [ ] CHECK COMPRESSOR OIL LEVELS
SWCH | SCREW CHILLER | FALL | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SWCH | SCREW CHILLER | FALL | LOAD CONDITION:
SWCH | SCREW CHILLER | FALL | A. DISCHARGE LINE TEMPERATURE:
SWCH | SCREW CHILLER | FALL | COMP #1 ________DEG.F COMP #2 ________DEG.F
SWCH | SCREW CHILLER | FALL | COMP #3 ________DEG.F COMP #4 ________DEG.F
SWCH | SCREW CHILLER | FALL | B. OUTSIDE AIR TEMP: ________DEG.F
SWCH | SCREW CHILLER | FALL | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | FALL | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | FALL | [ ] CHECK OUTDOOR COIL CONDITION
SWCH | SCREW CHILLER | FALL | [ ] CHECK OUTDOOR FAN CONDITION
SWCH | SCREW CHILLER | FALL | [ ] CHECK OUTDOOR FAN MOTOR
SWCH | SCREW CHILLER | FALL | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
SWCH | SCREW CHILLER | FALL | [ ] CHECK HOT GAS BY-PASS OPERATION
SWCH | SCREW CHILLER | FALL | [ ] CHECK CRANKCASE HEATERS
SWCH | SCREW CHILLER | FALL | [ ] CHANGE LEAD COMPRESSOR
SWCH | SCREW CHILLER | FALL | [ ] CHECK SEQUENCE OF OPERATION
SWCH | SCREW CHILLER | FALL | [ ] CHECK LIQUID LINE SIGHT GLASSES
SWCH | SCREW CHILLER | FALL | [ ] CHECK CONTROL SETPOINTS
SWCH | SCREW CHILLER | FALL | [ ] CHECK ALL MOTOR AMPS
SWCH | SCREW CHILLER | FALL | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SWCH | SCREW CHILLER | FALL | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SWCH | SCREW CHILLER | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SWCH | SCREW CHILLER | FALL | [ ] CHECK CAPACITY CONTROLS
SWCH | SCREW CHILLER | FALL | [ ] CHECK SAFETY CONTROLS
SWCH | SCREW CHILLER | FALL | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
SWCH | SCREW CHILLER | FALL | OUTLET________PSI
SWCH | SCREW CHILLER | WINTER | [ ] CHECK COMPRESSOR OIL LEVELS:
SWCH | SCREW CHILLER | WINTER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SWCH | SCREW CHILLER | WINTER | LOAD CONDITION:
SWCH | SCREW CHILLER | WINTER | A. DISCHARGE LINE TEMP:
SWCH | SCREW CHILLER | WINTER | COMP #1 ________DEG.F COMP #2 ________DEG.F
SWCH | SCREW CHILLER | WINTER | COMP #3 ________DEG.F COMP #4 ________DEG.F
SWCH | SCREW CHILLER | WINTER | B. OUTSIDE AIR TEMP: _________DEG.F
SWCH | SCREW CHILLER | WINTER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | WINTER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | WINTER | [ ] CHECK OUTDOOR COIL CONDITION
SWCH | SCREW CHILLER | WINTER | [ ] CHECK OUTDOOR FAN CONDITION
SWCH | SCREW CHILLER | WINTER | [ ] CHECK OUTDOOR FAN MOTOR
SWCH | SCREW CHILLER | WINTER | [ ] CHECK CRANKCASE HEATERS
SWCH | SCREW CHILLER | WINTER | [ ] CHANGE LEAD COMPRESSOR
SWCH | SCREW CHILLER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
SWCH | SCREW CHILLER | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASSES
SWCH | SCREW CHILLER | WINTER | [ ] CHECK CONTROL SET POINTS
SWCH | SCREW CHILLER | WINTER | [ ] CHECK ALL MOTORS AMPS
SWCH | SCREW CHILLER | WINTER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SWCH | SCREW CHILLER | WINTER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SWCH | SCREW CHILLER | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SWCH | SCREW CHILLER | WINTER | [ ] CHECK CHILLED WTR PRESSURE: INLET________PSI
SWCH | SCREW CHILLER | WINTER | OUTLET________PSI
SWCH | SCREW CHILLER | SPRING | [ ] CHECK COMPRESSOR OIL LEVELS:
SWCH | SCREW CHILLER | SPRING | [ ] OIL SAMPLE #1_____#2_____#3_____#4_____
SWCH | SCREW CHILLER | SPRING | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SWCH | SCREW CHILLER | SPRING | LOAD CONDITION:
SWCH | SCREW CHILLER | SPRING | A. DISCHARGE PRESSURE:
SWCH | SCREW CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SWCH | SCREW CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SWCH | SCREW CHILLER | SPRING | B. SUCTION PRESSURE:
SWCH | SCREW CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SWCH | SCREW CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SWCH | SCREW CHILLER | SPRING | C. NET OIL PRESSURE:
SWCH | SCREW CHILLER | SPRING | COMP #1 ________PSI COMP #2 ________PSI
SWCH | SCREW CHILLER | SPRING | COMP #3 ________PSI COMP #4 ________PSI
SWCH | SCREW CHILLER | SPRING | D. CIRCUIT SUPERHEAT:
SWCH | SCREW CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
SWCH | SCREW CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
SWCH | SCREW CHILLER | SPRING | E. SYSTEM SUBCOOLING:
SWCH | SCREW CHILLER | SPRING | CKT #1 ________DEG.F CKT #2 ________DEG.F
SWCH | SCREW CHILLER | SPRING | CKT #3 ________DEG.F CKT #4 ________DEG.F
SWCH | SCREW CHILLER | SPRING | F. DISCHARGE LINE TEMPERATURE:
SWCH | SCREW CHILLER | SPRING | COMP #1 ________DEG.F COMP #2 ________DEG.F
SWCH | SCREW CHILLER | SPRING | COMP #3 ________DEG.F COMP #4 ________DEG.F
SWCH | SCREW CHILLER | SPRING | G. OUTSIDE AIR TEMP: ________DEG.F
SWCH | SCREW CHILLER | SPRING | H. CHILLED WTR TEMP: IN________DEG.F
SWCH | SCREW CHILLER | SPRING | OUT________DEG.F
SWCH | SCREW CHILLER | SPRING | I. CONDENSER WATER TEMP: IN________DEG.F
SWCH | SCREW CHILLER | SPRING | OUT________DEG.F
SWCH | SCREW CHILLER | SPRING | [ ] CHECK OUTDOOR COIL CONDITION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK OUTDOOR FAN CONDITION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK OUTDOOR FAN MOTORS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK LOW AMBIENT DAMPERS FOR PROPER OPERATION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK TXV SENSING BULBS FOR CLEANLINESS & CONTACT
SWCH | SCREW CHILLER | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK CRANKCASE HEATERS
SWCH | SCREW CHILLER | SPRING | [ ] CHANGE LEAD COMPRESSOR
SWCH | SCREW CHILLER | SPRING | [ ] CHECK SEQUENCE OF OPERATION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASSES
SWCH | SCREW CHILLER | SPRING | [ ] CHECK CONTROL SET POINTS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK ALL MOTORS AMPS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SWCH | SCREW CHILLER | SPRING | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SWCH | SCREW CHILLER | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SWCH | SCREW CHILLER | SPRING | [ ] CHECK CAPACITY CONTROLS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK SAFETY CONTROLS
SWCH | SCREW CHILLER | SPRING | FREEZE PROTECTION____________
SWCH | SCREW CHILLER | SPRING | OIL FAILURE_____________
SWCH | SCREW CHILLER | SPRING | LOW AND HIGH PRESSURE_____________
SWCH | SCREW CHILLER | SPRING | FLOW SWITCH__________________
SWCH | SCREW CHILLER | SPRING | [ ] MEG OHM MOTOR 10 HP OR LARGER
SWCH | SCREW CHILLER | SPRING | [ ] CHECK CONTACTOR POINTS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
SWCH | SCREW CHILLER | SPRING | [ ] CHECK CHILLED WTR PRESS: IN________PSI
SWCH | SCREW CHILLER | SPRING | OUT________PSI
SWCH | SCREW CHILLER | SPRING | [ ] INSPECT RELIEF VALVE
SWCH | SCREW CHILLER | SPRING | [ ] CHANGE MOTOR COOLER REFRIGERANT DRIER (IF REQ)
SWCH | SCREW CHILLER | SPRING | [ ] CHANGE OIL STRAINER / OIL RETURN SYSTEM (IF REQ)
SWCH | SCREW CHILLER | SPRING | [ ] INSPECT FLOAT VALVE ASSEMBLY (IF REQ)
SWCH | SCREW CHILLER | SPRING | [ ] CHECK STARTER OVERLOADS AND TIME DELAYS
SWCH | SCREW CHILLER | SPRING | [ ] RECORD INFORMATION IN CUSTOMERS LOG
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK COMPRESSOR OIL LEVELS:
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK OPERATING PRESSURES AND TEMPERATURES AT FULL
SWCH | SCREW CHILLER | SUMMER | LOAD CONDITION:
SWCH | SCREW CHILLER | SUMMER | A. DISCHARGE LINE TEMPERATURE:
SWCH | SCREW CHILLER | SUMMER | COMP #1 ________DEG.F COMP #2 ________DEG.F
SWCH | SCREW CHILLER | SUMMER | COMP #3 ________DEG.F COMP #4 ________DEG.F
SWCH | SCREW CHILLER | SUMMER | B. OUTSIDE AIR TEMP: ________DEG.F
SWCH | SCREW CHILLER | SUMMER | C. CHILLED WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | SUMMER | D. CONDENSER WTR TEMP: IN________DEG.F OUT________DEG.F
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK OUTDOOR COIL CONDITION
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK OUTDOOR FAN CONDITION
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK OUTDOOR FAN MOTOR
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK CRANKCASE HEATERS
SWCH | SCREW CHILLER | SUMMER | [ ] CHANGE LEAD COMPRESSOR
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASSES
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK CONTROL SET POINTS
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK ALL MOTOR AMPS
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK SUPPLY VOLTAGE______,______,______.
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK FOR UNUSUAL NOISE AND VIBRATION
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK SAFETY CONTROLS
SWCH | SCREW CHILLER | SUMMER | [ ] CHECK CHILLED WTR PRESS. IN________PSI
SWCH | SCREW CHILLER | SUMMER | OUT________PSI
SWP | SUMP WATER PUMP | FALL | [ ] CHECK VOLTAGE__________________
SWP | SUMP WATER PUMP | FALL | [ ] CHECK AMPS_____________________
SWP | SUMP WATER PUMP | FALL | [ ] CHECK FOR UNUSUAL VIBRATION
SWP | SUMP WATER PUMP | FALL | [ ] CHECK MOTOR AND BEARING OIL LEVEL
SWP | SUMP WATER PUMP | FALL | [ ] CHECK FOR SEAL LEAK
SWP | SUMP WATER PUMP | FALL | [ ] ALTERNATE LEAD / LAG PUMP
SWP | SUMP WATER PUMP | FALL | [ ] LUBRICATE BEARING ASSEMBLY (PER MFG SPECS)
SWP | SUMP WATER PUMP | FALL | [ ] VISUAL INSPECTION OF COUPLING FOR ABNORMAL WEAR
SWP | SUMP WATER PUMP | FALL | [ ] LUBRICATE PUMP MOTOR AND BEARINGS (PER MFG SPECS)
SWP | SUMP WATER PUMP | FALL | [ ] CHECK AUTOMATIC STAND-BY CHANGEOVER
SWP | SUMP WATER PUMP | FALL | [ ] CHECK FLUID LEVEL CONTROL
SWP | SUMP WATER PUMP | FALL | [ ] CHECK SAFETIES AND ALARMS
SWP | SUMP WATER PUMP | FALL | [ ] CHECK OPERATION OF FLOAT
SWP | SUMP WATER PUMP | FALL | [ ] FILL SUMP WELL WITH WATER AND VERIFY PUMP OPERATION
SWP | SUMP WATER PUMP | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION
SWP | SUMP WATER PUMP | WINTER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
SWP | SUMP WATER PUMP | WINTER | [ ] CHECK FOR SEAL LEAK
SWP | SUMP WATER PUMP | WINTER | [ ] ALTERNATE LEAD / LAG PUMP
SWP | SUMP WATER PUMP | WINTER | [ ] CHECK VOLTAGE__________________
SWP | SUMP WATER PUMP | WINTER | [ ] CHECK AMPS_____________________
SWP | SUMP WATER PUMP | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION
SWP | SUMP WATER PUMP | SPRING | [ ] CHECK MOTOR AND BEARING OIL LEVEL
SWP | SUMP WATER PUMP | SPRING | [ ] CHECK FOR SEAL LEAK
SWP | SUMP WATER PUMP | SPRING | [ ] ALTERNATE LEAD / LAG PUMP
SWP | SUMP WATER PUMP | SPRING | [ ] LUBRICATE BEARING ASSEMBLY (PER MFG SPECS)
SWP | SUMP WATER PUMP | SPRING | [ ] CHECK VOLTAGE____________________
SWP | SUMP WATER PUMP | SPRING | [ ] CHECK AMPS_______________________
SWP | SUMP WATER PUMP | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION
SWP | SUMP WATER PUMP | SUMMER | [ ] CHECK MOTOR AND BEARING OIL LEVEL
SWP | SUMP WATER PUMP | SUMMER | [ ] CHECK FOR SEAL LEAK
SWP | SUMP WATER PUMP | SUMMER | [ ] ALTERNATE LEAD / LAG PUMP
SWP | SUMP WATER PUMP | SUMMER | [ ] CHECK VOLTAGE___________________
SWP | SUMP WATER PUMP | SUMMER | [ ] CHECK AMPS______________________
TC | TIME CLOCK | FALL | [ ] CHECK DATE
TC | TIME CLOCK | FALL | [ ] CHECK TIME OF DAY
TC | TIME CLOCK | FALL | [ ] PROGRAM IN NEW DAYLIGHT SAVINGS TIME START & END DATE
TC | TIME CLOCK | FALL | [ ] CHECK TEMPERATURE SETTING OF NIGHT SET-BACK
TC | TIME CLOCK | FALL | [ ] GET LIST AND VERIFY HOLIDAY DATES WITH MANAGER OR
TC | TIME CLOCK | FALL | CONTACT PERSON ON SITE
TC | TIME CLOCK | FALL | [ ] CHECK AND SET HOLIDAYS FOR NEXT 12 MONTHS
TC | TIME CLOCK | FALL | LIST NEW DATES BELOW:
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | __________________________________________________________
TC | TIME CLOCK | FALL | [ ] DELETE OLD HOLIDAY DATES
TC | TIME CLOCK | WINTER | [ ] CHECK DATE
TC | TIME CLOCK | WINTER | [ ] CHECK TIME OF DAY
TC | TIME CLOCK | WINTER | [ ] CHECK TEMPERATURE SETTINGS OF NIGHT SET-BACK
TC | TIME CLOCK | WINTER | [ ] PROGRAM IN NEW DAYLIGHT SAVINGS START & END DATES
TC | TIME CLOCK | WINTER | [ ] GET LIST AND VERIFY HOLIDAY DATES WITH MANAGER OR
TC | TIME CLOCK | WINTER | CONTACT PERSON ON SITE
TC | TIME CLOCK | WINTER | [ ] PROGRAM NEW HOLIDAYS FOR THE NEXT 12 MONTHS
TC | TIME CLOCK | WINTER | LIST NEW HOLIDAYS BELOW:
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | __________________________________________________________
TC | TIME CLOCK | WINTER | [ ] DELETE OLD HOLIDAY DATES
TC | TIME CLOCK | SPRING | [ ] CHECK DATE
TC | TIME CLOCK | SPRING | [ ] CHECK TIME OF DAY
TC | TIME CLOCK | SPRING | [ ] CHECK TEMPERATURE SETTINGS OF NIGHT SET-BACK
TC | TIME CLOCK | SPRING | [ ] PROGRAM IN NEW DAYLIGHT SAVINGS START & END DATES
TC | TIME CLOCK | SPRING | [ ] GET LIST AND VERIFY HOLIDAY DATES WITH MANAGER OR
TC | TIME CLOCK | SPRING | CONTACT PERSON ON SITE
TC | TIME CLOCK | SPRING | [ ] CHECK AND SET HOLIDAYS FOR THE NEXT 12 MONTHS
TC | TIME CLOCK | SPRING | LIST NEW HOLIDAY DATES BELOW:
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | __________________________________________________________
TC | TIME CLOCK | SPRING | [ ] DELETE OLD HOLIDAY DATES
TC | TIME CLOCK | SUMMER | [ ] CHECK DATE
TC | TIME CLOCK | SUMMER | [ ] CHECK TIME OF DAY
TP | TRAP PRIMER | FALL | [ ] CHECK FOR WATER LEAKS
TP | TRAP PRIMER | FALL | [ ] CHECK FOR AUTOMATIC WATER VALVE
TP | TRAP PRIMER | WINTER | [ ] CHECK FOR WATER LEAKS
TP | TRAP PRIMER | WINTER | [ ] CHECK FOR AUTOMATIC WATER VALVE
TP | TRAP PRIMER | SPRING | [ ] CHECK FOR WATER LEAKS
TP | TRAP PRIMER | SPRING | [ ] CHECK FOR AUTOMATIC WATER VALVE
TP | TRAP PRIMER | SUMMER | [ ] CHECK FOR WATER LEAKS
TP | TRAP PRIMER | SUMMER | [ ] CHECK FOR AUTOMATIC WATER VALVE
TUBE | TUBE RODDING | FALL | [ ] ISOLATE AND DRAIN HEAT EXCHANGER
TUBE | TUBE RODDING | FALL | [ ] REMOVE END BELLS
TUBE | TUBE RODDING | FALL | [ ] INSPECT TUBES FOR DEBRIS
TUBE | TUBE RODDING | FALL | [ ] CLEAN TUBES WITH RODDING MACHINE
TUBE | TUBE RODDING | FALL | [ ] RE-INSTALL END BELLS
TUBE | TUBE RODDING | FALL | [ ] RE-FILL AND PURGE AIR FROM HEAT EXCHANGER
TUBE | TUBE RODDING | WINTER | [ ] ISOLATE AND DRAIN HEAT EXCHANGER
TUBE | TUBE RODDING | WINTER | [ ] REMOVE END BELLS
TUBE | TUBE RODDING | WINTER | [ ] INSPECT TUBES FOR DEBRIS
TUBE | TUBE RODDING | WINTER | [ ] CLEAN TUBES WITH RODDING MACHINE
TUBE | TUBE RODDING | WINTER | [ ] RE-INSTALL END BELLS
TUBE | TUBE RODDING | WINTER | [ ] RE-FILL AND PURGE AIR FROM HEAT EXCHANGER
TUBE | TUBE RODDING | SPRING | [ ] ISOLATE AND DRAIN HEAT EXCHANGER
TUBE | TUBE RODDING | SPRING | [ ] REMOVE END BELLS
TUBE | TUBE RODDING | SPRING | [ ] INSPECT TUBES FOR DEBRIS
TUBE | TUBE RODDING | SPRING | [ ] CLEAN TUBES WITH RODDING MACHINE
TUBE | TUBE RODDING | SPRING | [ ] RE-INSTALL END BELLS
TUBE | TUBE RODDING | SPRING | [ ] RE-FILL AND PURGE AIR FROM HEAT EXCHANGER
TUBE | TUBE RODDING | SUMMER | [ ] ISOLATE AND DRAIN HEAT EXCHANGER
TUBE | TUBE RODDING | SUMMER | [ ] REMOVE END BELLS
TUBE | TUBE RODDING | SUMMER | [ ] INSPECT TUBES FOR DEBRIS
TUBE | TUBE RODDING | SUMMER | [ ] CLEAN TUBES WITH RODDING MACHINE
TUBE | TUBE RODDING | SUMMER | [ ] RE-INSTALL END BELLS
TUBE | TUBE RODDING | SUMMER | [ ] RE-FILL AND PURGE AIR FROM HEAT EXCHANGER
UH | UNIT HEATER | FALL | [ ] CHECK FAN OPERATION
UH | UNIT HEATER | FALL | [ ] CHECK THERMOSTAT OPERATION
UH | UNIT HEATER | FALL | [ ] CHECK ALL CONTROLS
UH | UNIT HEATER | FALL
UH | UNIT HEATER | FALL | ELECTRIC HEAT
UH | UNIT HEATER | FALL
UH | UNIT HEATER | FALL | [ ] CHECK AMP DRAWS___________________AMPS
UH | UNIT HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
UH | UNIT HEATER | FALL | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | FALL | GAS HEAT
UH | UNIT HEATER | FALL
UH | UNIT HEATER | FALL | [ ] VISUAL CHECK OF HEAT EXCHANGERS AND FLUE
UH | UNIT HEATER | FALL | [ ] CHECK PILOT SETTING
UH | UNIT HEATER | FALL | [ ] CHECK MAIN GAS PRESSURE
UH | UNIT HEATER | FALL | [ ] CHECK MANIFOLD GAS PRESSURE
UH | UNIT HEATER | FALL | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | WINTER | [ ] CHECK FAN OPERATION
UH | UNIT HEATER | WINTER | [ ] CHECK THERMOSTAT OPERATION
UH | UNIT HEATER | WINTER | [ ] CHECK ALL CONTROLS
UH | UNIT HEATER | WINTER
UH | UNIT HEATER | WINTER | ELECTRIC HEAT
UH | UNIT HEATER | WINTER
UH | UNIT HEATER | WINTER | [ ] CHECK AMP DRAW___________________AMPS
UH | UNIT HEATER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | WINTER | GAS HEAT
UH | UNIT HEATER | WINTER
UH | UNIT HEATER | WINTER | [ ] VISUAL CHECK OF HEAT EXCHANGER AND FLUE
UH | UNIT HEATER | WINTER | [ ] CHECK PILOT SETTING
UH | UNIT HEATER | WINTER | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | SPRING | [ ] CHECK FAN OPERATION
UH | UNIT HEATER | SPRING | [ ] CHECK THERMOSTAT OPERATION
UH | UNIT HEATER | SPRING | [ ] CHECK ALL CONTROLS
UH | UNIT HEATER | SPRING
UH | UNIT HEATER | SPRING | ELECTRIC HEAT
UH | UNIT HEATER | SPRING
UH | UNIT HEATER | SPRING | [ ] CHECK AMP DRAW______________________AMPS
UH | UNIT HEATER | SPRING | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | SPRING | GAS HEAT
UH | UNIT HEATER | SPRING
UH | UNIT HEATER | SPRING | [ ] VISUAL CHECK OF HEAT EXCHANGER AND FLUE
UH | UNIT HEATER | SPRING | [ ] CHECK PILOT SETTING
UH | UNIT HEATER | SPRING | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | SUMMER | [ ] CHECK FAN OPERATION
UH | UNIT HEATER | SUMMER | [ ] CHECK THERMOSTAT OPERATION
UH | UNIT HEATER | SUMMER | [ ] CHECK ALL CONTROLS
UH | UNIT HEATER | SUMMER
UH | UNIT HEATER | SUMMER | ELECTRIC HEAT
UH | UNIT HEATER | SUMMER
UH | UNIT HEATER | SUMMER | [ ] CHECK AMP DRAW_______________________AMPS
UH | UNIT HEATER | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
UH | UNIT HEATER | SUMMER | GAS HEAT
UH | UNIT HEATER | SUMMER
UH | UNIT HEATER | SUMMER | [ ] VISUAL CHECK OF HEAT EXCHANGER AND FLUE
UH | UNIT HEATER | SUMMER | [ ] CHECK PILOT SETTING
UH | UNIT HEATER | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
UV | UNIT VENTILATOR | FALL | [ ] CHECK BLOWER BELT
UV | UNIT VENTILATOR | FALL | [ ] CHECK PULLEY WEAR
UV | UNIT VENTILATOR | FALL | [ ] CHECK FRESH AIR DAMPER OPERATION
UV | UNIT VENTILATOR | FALL | [ ] CHECK OPERATING SEQUENCE
UV | UNIT VENTILATOR | FALL | [ ] CHECK THERMOSTAT OPERATION
UV | UNIT VENTILATOR | FALL | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
UV | UNIT VENTILATOR | FALL | [ ] INSPECT CONDITION OF COIL
UV | UNIT VENTILATOR | FALL | [ ] CHECK VOLTAGE_______________
UV | UNIT VENTILATOR | FALL | [ ] CHECK AMPS_________________
UV | UNIT VENTILATOR | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
UV | UNIT VENTILATOR | FALL | [ ] CHECK CONTACTOR POINTS
UV | UNIT VENTILATOR | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
UV | UNIT VENTILATOR | FALL | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
UV | UNIT VENTILATOR | FALL | [ ] CHECK ELECTRIC HEAT OPERATION (IF EQUIPPED)
UV | UNIT VENTILATOR | FALL | [ ] CHECK HOT WATER COIL OPERATION (IF EQUIPPED)
UV | UNIT VENTILATOR | WINTER | [ ] CHECK BLOWER BELT
UV | UNIT VENTILATOR | WINTER | [ ] CHECK PULLEY WEAR
UV | UNIT VENTILATOR | WINTER | [ ] CHECK FRESH AIR DAMPER OPERATION
UV | UNIT VENTILATOR | WINTER | [ ] CHECK OPERATING SEQUENCE
UV | UNIT VENTILATOR | WINTER | [ ] CHECK THERMOSTAT OPERATION
UV | UNIT VENTILATOR | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
UV | UNIT VENTILATOR | WINTER | [ ] INSPECT CONDITION OF COIL
UV | UNIT VENTILATOR | WINTER | [ ] CHECK VOLTAGE____________________
UV | UNIT VENTILATOR | WINTER | [ ] CHECK AMPS_______________________
UV | UNIT VENTILATOR | SPRING | [ ] CHECK CONDENSATE PAN
UV | UNIT VENTILATOR | SPRING | [ ] ADD PAN TABLETS
UV | UNIT VENTILATOR | SPRING | [ ] CHECK CHILLED WATER COIL IF EQUIPPED
UV | UNIT VENTILATOR | SPRING | [ ] LUBRICATE BLOWER BEARINGS (PER MFG SPECS)
UV | UNIT VENTILATOR | SPRING | [ ] CHECK BLOWER BELT
UV | UNIT VENTILATOR | SPRING | [ ] CHECK PULLEY WEAR
UV | UNIT VENTILATOR | SPRING | [ ] CHECK FRESH AIR DAMPER OPERATION
UV | UNIT VENTILATOR | SPRING | [ ] CHECK OPERATING SEQUENCE
UV | UNIT VENTILATOR | SPRING | [ ] CHECK THERMOSTAT OPERATION
UV | UNIT VENTILATOR | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
UV | UNIT VENTILATOR | SPRING | [ ] INSPECT CONDITION OF COIL
UV | UNIT VENTILATOR | SPRING | [ ] CHECK VOLTAGE_______________________
UV | UNIT VENTILATOR | SPRING | [ ] CHECK AMPS_____________________
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK BLOWER BELT
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK PULLEY WEAR
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK FRESH AIR DAMPER OPERATION
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK OPERATING SEQUENCE
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK THERMOSTAT OPERATION
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
UV | UNIT VENTILATOR | SUMMER | [ ] INSPECT CONDITION OF COIL
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK VOLTAGE___________________
UV | UNIT VENTILATOR | SUMMER | [ ] CHECK AMPS_______________________
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK DAMPER OPERATION
VAV | VAV TERMINAL UNIT | FALL | [ ] INSPECT LINKAGE
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK ELECTRIC HEAT OPERATION
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK HEAT TEMPERATURE RISE_________________-
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK CONTACTOR POINT
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK VOLTAGE_____________________
VAV | VAV TERMINAL UNIT | FALL | [ ] CHECK AMP DRAW___________________
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK DAMPER OPERATION
VAV | VAV TERMINAL UNIT | WINTER | [ ] INSPECT LINKAGE
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK ELECTRIC HEAT OPERATION
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK HEAT TEMPERATURE RISE_________________-
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK ELECTICAL CONNECTIONS
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK CONTACTOR POINT
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK VOLTAGE______________________
VAV | VAV TERMINAL UNIT | WINTER | [ ] CHECK AMP DRAW______________________
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK DAMPER OPERATION
VAV | VAV TERMINAL UNIT | SPRING | [ ] INSPECT LINKAGE
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK ELECTRIC HEAT OPERATION
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK HEAT TEMPERATURE RISE________________-
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK CONTACTOR POINT
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK VOLTAGE____________________
VAV | VAV TERMINAL UNIT | SPRING | [ ] CHECK AMPS DRAW___________________
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
VAV | VAV TERMINAL UNIT | SUMMER | [ ] INSPECT LINKAGE
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRIC HEAT OPERATION
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK HEAT TEMPERATURE RISE______________
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK CONTACTOR POINT
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK VOLTAGE__________________
VAV | VAV TERMINAL UNIT | SUMMER | [ ] CHECK AMP DRAW__________________
VP | VACUUM PUMP | FALL | [ ] CHECK BELT
VP | VACUUM PUMP | FALL | [ ] CHECK PULLEY WEAR
VP | VACUUM PUMP | FALL | [ ] LOG RUN HOURS
VP | VACUUM PUMP | FALL | [ ] PERFORM REQUIRED SERVICE FOR RUN HOURS
VP | VACUUM PUMP | FALL | (PER MFG SPECS)
VP | VACUUM PUMP | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VP | VACUUM PUMP | FALL | [ ] CHECK VOLTAGE___________________
VP | VACUUM PUMP | FALL | [ ] CHECK AMPS______________________
VP | VACUUM PUMP | FALL | [ ] CHECK OIL LEVEL
VP | VACUUM PUMP | FALL | [ ] FILL OUT MANUFACTURERS CHECK SHEETS
VP | VACUUM PUMP | FALL | [ ] ANNUAL SERVICE (PER MFG REQUIREMENTS)
VP | VACUUM PUMP | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
VP | VACUUM PUMP | FALL | [ ] CHECK CONTACTOR POINTS
VP | VACUUM PUMP | FALL | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
VP | VACUUM PUMP | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
VP | VACUUM PUMP | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
VP | VACUUM PUMP | FALL | [ ] TEST OIL
VP | VACUUM PUMP | WINTER | [ ] CHECK BELT
VP | VACUUM PUMP | WINTER | [ ] CHECK PULLEY WEAR
VP | VACUUM PUMP | WINTER | [ ] LOG RUN HOURS
VP | VACUUM PUMP | WINTER | [ ] PERFORM REQUIRED SERVICE FOR RUN HOURS
VP | VACUUM PUMP | WINTER | (PER MFG SPECS)
VP | VACUUM PUMP | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VP | VACUUM PUMP | WINTER | [ ] CHECK VOLTAGE______________________
VP | VACUUM PUMP | WINTER | [ ] CHECK AMPS_________________________
VP | VACUUM PUMP | WINTER | [ ] CHECK OIL LEVEL
VP | VACUUM PUMP | WINTER | [ ] FILL OUT MANUFACTURERS CHECK SHEETS
VP | VACUUM PUMP | WINTER | [ ] CHECK INLINE FILTERS IF APPLICABLE
VP | VACUUM PUMP | SPRING | [ ] CHECK BELT
VP | VACUUM PUMP | SPRING | [ ] CHECK PULLEY WEAR
VP | VACUUM PUMP | SPRING | [ ] LOG RUN HOURS
VP | VACUUM PUMP | SPRING | [ ] PERFORM REQUIRED SERVICE FOR RUN HOURS
VP | VACUUM PUMP | SPRING | (PER MFG SPECS)
VP | VACUUM PUMP | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
VP | VACUUM PUMP | SPRING | [ ] CHECK VOLTAGE__________________
VP | VACUUM PUMP | SPRING | [ ] CHECK AMPS______________________
VP | VACUUM PUMP | SPRING | [ ] CHECK OIL LEVEL
VP | VACUUM PUMP | SPRING | [ ] FILL OUT MANUFACTURERS CHECK SHEETS
VP | VACUUM PUMP | SUMMER | [ ] CHECK BELT
VP | VACUUM PUMP | SUMMER | [ ] CHECK PULLEY WEAR
VP | VACUUM PUMP | SUMMER | [ ] LOG RUN HOURS
VP | VACUUM PUMP | SUMMER | [ ] PERFORM REQUIRED SERVICE FOR RUN HOURS
VP | VACUUM PUMP | SUMMER | (PER MFG SPECS)
VP | VACUUM PUMP | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VP | VACUUM PUMP | SUMMER | [ ] CHECK VOLTAGE______________________
VP | VACUUM PUMP | SUMMER | [ ] CHECK AMPS__________________________
VP | VACUUM PUMP | SUMMER | [ ] CHECK OIL LEVEL
VP | VACUUM PUMP | SUMMER | [ ] FILL OUT MANUFACTURERS CHECK SHEETS
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK CABINET FILTER
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK CABINET TEMPERATURE CONTROL
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK HEATER
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK FAN OPERATION
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK HERTZ OUTPUT
VSD | VARIABLE SPEED DRIVE | FALL | [ ] CHECK VOLTAGE
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK CABINET FILTER
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK CABINET TEMPERATURE CONTROL
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK HEATER
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK FAN OPERATION
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK HERTZ OUTPUT
VSD | VARIABLE SPEED DRIVE | WINTER | [ ] CHECK VOLTAGE
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK CABINET FILTER
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK CABINET TEMPERATURE CONTROL
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK HEATER
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK FAN OPERATION
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK HERTZ OUTPUT
VSD | VARIABLE SPEED DRIVE | SPRING | [ ] CHECK VOLTAGE
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK CABINET FILTER
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK CABINET TEMPERATURE CONTROL
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK HEATER
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK FAN OPERATION
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK HERTZ OUTPUT
VSD | VARIABLE SPEED DRIVE | SUMMER | [ ] CHECK VOLTAGE
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK DAMPER OPERATION
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] INSPECT LINKAGE
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK ELECTRIC HEAT OPERATION
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK HEAT TEMPERATURE RISE________________
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK CONTACTOR POINTS
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK VOLTAGE_________________
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK AMP DRAW_________________
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] CHECK FAN OPERATION
VVR | VAV REHEAT TERMINAL UNIT | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK DAMPER OPERATION
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] INSPECT LINKAGE
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK ELECTRIC HEAT OPERATION
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK HEAT TEMPERATURE RISE__________________
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK CONTACTOR POINTS
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK VOLTAGE________________
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK AMP DRAW_________________
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] CHECK FAN OPERATION
VVR | VAV REHEAT TERMINAL UNIT | WINTER | [ ] LUBRICATION MOTOR BEARINGS (PER MFG SPECS)
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK DAMPER OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] INSPECT LINKAGE
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK ELECTRIC HEAT OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK HEAT TEMPERATURE RISE________________
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK VOLTAGE_________________
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK AMP DRAW_________________
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] CHECK FAN OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SPRING | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] INSPECT LINKAGE
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRIC HEAT OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK HEAT TEMPERATURE RISE______________
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTION
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK CONTACTOR POINTS
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK VOLTAGE_____________
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK AMP DRAW______________
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] CHECK FAN OPERATION
VVR | VAV REHEAT TERMINAL UNIT | SUMMER | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK DAMPER OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] INSPECT LINKAGE
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK ELECTRIC HEAT OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK HEAT TEMPERATURE RISE_________________
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK CONTACTOR POINTS
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK SEQUENCE OF OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK VOLTAGE_______________________
VVT | VARIABLE VOLUME TERMINAL UNIT | FALL | [ ] CHECK AMP DRAW_________________________
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK DAMPER OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] INSPECT LINKAGE
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK ELECTRIC HEAT OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK HEAT TEMPERATURE RISE___________________
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK ELECTRIC CONNECTIONS
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK CONTACTOR POINTS
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK VOLTAGE___________________
VVT | VARIABLE VOLUME TERMINAL UNIT | WINTER | [ ] CHECK AMP DRAW_____________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK DAMPER OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] INSPECT LINKAGE
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK ELECTRIC HEAT OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK HEAT TEMPERATURE RISE____________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK SEQUENCE OF OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK VOLTAGE_________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SPRING | [ ] CHECK AMP DRAW______________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK DAMPER OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] INSPECT LINKAGE
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRIC HEAT OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK HEAT TEMPERATURE RISE____________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK CONTACTOR POINTS
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK SEQUENCE OF OPERATION
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK VOLTAGE_____________________
VVT | VARIABLE VOLUME TERMINAL UNIT | SUMMER | [ ] CHECK AMP DRAW_______________________
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK AIR FILTER AND CLEAN OR REPLACE AS NEEDED
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK OUTDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK INDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK FRESH AIR DAMPER OPERATION
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK TEMPERATURE DROP ACROSS COIL
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK TEMPERATURE RISE *IF HEAT PUMP
WAC | WINDOW AIR CONDITIONER | FALL | [ ] CHECK AND CLEAN BLOWER WHEELS
WAC | WINDOW AIR CONDITIONER | FALL | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK AIR FILTER AND CLEAN OR REPLACE AS NEEDED
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK OUTDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK INDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK FRESH AIR DAMPER OPERATION
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK TEMPERATURE DROP ACROSS COIL
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK TEMPERATURE RISE *IF HEAT PUMP
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] CHECK AND CLEAN BLOWER WHEELS
WAC | WINDOW AIR CONDITIONER | WINTER | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK AIR FILTER AND CLEAN OR REPLACE AS NEEDED
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK OUTDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK INDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK FRESH AIR DAMPER OPERATION
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK TEMPERATURE DROP ACROSS COIL
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK TEMPERATURE RISE *IF HEAT PUMP
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] CHECK AND CLEAN BLOWER WHEELS
WAC | WINDOW AIR CONDITIONER | SPRING | [ ] LUBRICATE MOTOR BEARING (PER MFG SPECS)
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK AIR FILTER AND CLEAN OR REPLACE AS NEEDED
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK OUTDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK INDOOR COIL CONDITION
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK FRESH AIR DAMPER OPERATIONS
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK TEMPERATURE DROP ACROSS COIL
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK TEMPERATURE RISE *IF HEAT PUMP
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] CHECK AND CLEAN BLOWER WHEELS
WAC | WINDOW AIR CONDITIONER | SUMMER | [ ] LUBRICATE MOTOR BEARINGS (PER MFG SPECS)
WC | WATER COOLER | FALL | [ ] CHECK CONDITION OF CONDENSER COIL
WC | WATER COOLER | FALL | [ ] CHECK CONDENSER FAN OPERATION
WC | WATER COOLER | FALL | [ ] CHECK FOR PROPER WATER FLOW
WC | WATER COOLER | FALL | [ ] CHECK COMPRESSOR OPERATION
WC | WATER COOLER | FALL | [ ] CHECK FOR PROPER DRAIN OPERATION
WC | WATER COOLER | FALL | [ ] CHECK COLD WATER
WC | WATER COOLER | WINTER | [ ] CHECK CONDITION OF CONDENSER COIL
WC | WATER COOLER | WINTER | [ ] CHECK CONDENSER FAN OPERATION
WC | WATER COOLER | WINTER | [ ] CHECK FOR PROPER WATER FLOW
WC | WATER COOLER | WINTER | [ ] CHECK COMPRESSOR OPERATION
WC | WATER COOLER | WINTER | [ ] CHECK FOR PROPER DRAIN OPERATION
WC | WATER COOLER | WINTER | [ ] CHECK COLD WATER
WC | WATER COOLER | SPRING | [ ] CHECK CONDITION OF CONDENSER COIL
WC | WATER COOLER | SPRING | [ ] CHECK CONDENSER FAN OPERATION
WC | WATER COOLER | SPRING | [ ] CHECK FOR PROPER WATER FLOW
WC | WATER COOLER | SPRING | [ ] CHECK COMPRESSOR OPERATION
WC | WATER COOLER | SPRING | [ ] CHECK FOR PROPER DRAIN OPERATION
WC | WATER COOLER | SPRING | [ ] CHECK COLD WATER
WC | WATER COOLER | SUMMER | [ ] CHECK CONDITION OF CONDENSER COIL
WC | WATER COOLER | SUMMER | [ ] CHECK CONDENSER FAN OPERATION
WC | WATER COOLER | SUMMER | [ ] CHECK FOR PROPER WATER FLOW
WC | WATER COOLER | SUMMER | [ ] CHECK COMPRESSOR OPERATION
WC | WATER COOLER | SUMMER | [ ] CHECK FOR PROPER DRAIN OPERATION
WC | WATER COOLER | SUMMER | [ ] CHECK COLD WATER
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK BELTS AND ADJUST
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
WCAC | WATER COOLED AC UNIT | FALL | [ ] ADD PAN TABS
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK INDOOR COIL CONDITION
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK SUPPLY VOLTAGE_________,_________,_________
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK SUPPLY MOTOR AMPS___________,_________,________
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK ECONOMIZER OPERATION
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK RELIEF DAMPERS
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK CONTROL SET POINTS
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK CRANKCASE HEATER
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK COMPRESSOR OIL LEVEL
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK INDOOR COIL TEMPERATURE DROP________DEG.F
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK COMPRESSOR DISCHARGE
WCAC | WATER COOLED AC UNIT | FALL | TEMPERATURE #1___________#2_________DEG.F
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCAC | WATER COOLED AC UNIT | FALL | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK ECONOMIZER CONTROL CALIBRATION
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK PULLEY WEAR
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK MINIMUM AIR SETTINGS (ECONOMIZER)
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK ECONOMIZER DAMPERS AND LINKAGE FOR
WCAC | WATER COOLED AC UNIT | FALL | BINDING AND LUBE
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK FRESH AIR SCREENS
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK HOT GAS BYPASS OPERATION
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK WATER SIDE ECONOMIZER
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCAC | WATER COOLED AC UNIT | FALL | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK BELTS AND ADJUST
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
WCAC | WATER COOLED AC UNIT | WINTER | [ ] ADD PAN TABS
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK INDOOR COIL CONDITION
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK SUPPLY VOLTAGE _________,_________,_________
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK SUPPLY MOTOR AMPS__________,_________,_________
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK ECONOMIZER OPERATION
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK RELIEF DAMPERS
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK CONTROL SET POINTS
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK CRANKCASE HEATER
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK COMPRESSOR OIL LEVEL
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK FRESH AIR INTAKE SCREENS
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK HOT GAS BYPASS OPERATION
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK WATER SIDE ECONOMIZER
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCAC | WATER COOLED AC UNIT | WINTER | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK BELTS AND ADJUST
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK PAN TABS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK INDOOR COIL CONDITION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE_________,__________,_________
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK SUPPLY MOTOR AMPS_________,__________,_________
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK ECONOMIZER OPERATION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK RELIEF DAMPERS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CONTROL SET POINTS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK COMPRESSOR OIL LEVEL
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK INDOOR COIL TEMP DROP #1____DEG.F #2____DEG.F
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK COMPRESSOR DISCHARGE
WCAC | WATER COOLED AC UNIT | SPRING | TEMPERATURE #1______DEG.F #2______DEG.F
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCAC | WATER COOLED AC UNIT | SPRING | [ ] LUBE BLOWER BEARINGS (IF REQUIRED)
WCAC | WATER COOLED AC UNIT | SPRING | [ ] LUBE BLOWER MOTOR
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE
WCAC | WATER COOLED AC UNIT | SPRING | #1_________DEG.F #2_________DEG.F
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK SUB COOLING #1__________#2__________
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT
WCAC | WATER COOLED AC UNIT | SPRING | AND BULB #1_________DEG.F #2__________DEG.F
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CAPACITY CONTROLS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK OPERATING CONTROLS PRESSURE SETTING
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK SAFETIES
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK OPERATING PRESSURES
WCAC | WATER COOLED AC UNIT | SPRING | #1 DISCH______(PSI) SUC_______(PSI)
WCAC | WATER COOLED AC UNIT | SPRING | #2 DISCH______(PSI) SUC_______(PSI)
WCAC | WATER COOLED AC UNIT | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
WCAC | WATER COOLED AC UNIT | SPRING | #1___________#2____________BLR______________
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK BLOWER WHEEL FOR DIRT
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK FRESH AIR INTAKE SCREENS
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK WATER SIDE ECONOMIZER
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
WCAC | WATER COOLED AC UNIT | SPRING | [ ] CHECK FLOW SWITCH OPERATION
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK BELTS AND ADJUST
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK CONDENSATE PAN, PUMP, AND TRAP
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] ADD PAN TABS
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK INDOOR COIL CONDITION
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK SUPPLY VOLTAGE_______,_______,________
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK SUPPLY MOTOR AMPS________,_______,________
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK ECONOMIZER OPERATION
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK RELIEF DAMPERS
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK CONTROL SET POINTS
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK COMPRESSOR OIL LEVEL
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK INDOOR COIL
WCAC | WATER COOLED AC UNIT | SUMMER | TEMPERATURE DROP #1________DEG.F #2_________DEG.F
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE
WCAC | WATER COOLED AC UNIT | SUMMER | #1__________DEG.F #2__________DEG.F
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK FRESH AIR INTAKE SCREENS
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK HOT GAS BYPASS OPERATION
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK WATER SIDE ECONOMIZER
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCAC | WATER COOLED AC UNIT | SUMMER | [ ] CHECK VFD, INLET/DISCHARGE VANE OPERATION
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK SUPPLY VOLTAGE_________,_________,_________
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK CONTROL SET POINTS
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK CRANKCASE HEATER
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK COMPRESSOR OIL LEVEL
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK LIQUID LINE SIGHT GLASS
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK INDOOR COIL TEMPERATURE DROP________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK COMPRESSOR DISCHARGE
WCCU | WATER COOLED CONDENSING UNIT | FALL | TEMPERATURE #1___________#2_________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK HOT GAS BYPASS OPERATION
WCCU | WATER COOLED CONDENSING UNIT | FALL | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK SUPPLY VOLTAGE _________,_________,_________
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK CONTROL SET POINTS
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK CRANKCASE HEATER
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK COMPRESSOR OIL LEVEL
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK LIQUID LINE SIGHT GLASS
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK SEQUENCE OF OPERATION
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK HOT GAS BYPASS OPERATION
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK WATER SIDE ECONOMIZER
WCCU | WATER COOLED CONDENSING UNIT | WINTER | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK SUPPLY VOLTAGE_________,__________,_________
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CONTROL SET POINTS
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CRANKCASE HEATER
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK COMPRESSOR OIL LEVEL
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK LIQUID LINE SIGHT GLASS
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK INDOOR COIL TEMP DROP #1____DEG.F #2____DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK COMPRESSOR DISCHARGE
WCCU | WATER COOLED CONDENSING UNIT | SPRING | TEMPERATURE #1______DEG.F #2______DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK COMPRESSOR SUCTION TEMPERATURE
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #1_________DEG.F #2_________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK SUB COOLING #1__________#2__________
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK EXPANSION VALVE SUPERHEAT
WCCU | WATER COOLED CONDENSING UNIT | SPRING | AND BULB #1_________DEG.F #2__________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CAPACITY CONTROLS
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK OPERATING CONTROLS PRESSURE SETTING
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK SAFETIES
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK OPERATING PRESSURES
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #1 DISCH______(PSI) SUC_______(PSI)
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #2 DISCH______(PSI) SUC_______(PSI)
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] MEGG/OHM MOTORS 10.0 HP OR LARGER
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #1__________________#2____________________
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CONTACTOR POINTS
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CONTACTOR POINT VOLTAGE DROP
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK HOT GAS BYPASS OPERATION
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK FLOW SWITCH OPERATION
WCCU | WATER COOLED CONDENSING UNIT | SPRING | [ ] CHECK CONDENSER WATER TEMPERATURE
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #1 IN__________OUT____________
WCCU | WATER COOLED CONDENSING UNIT | SPRING | #2 IN__________OUT____________
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK UNUSUAL VIBRATION / NOISE
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK SUPPLY VOLTAGE_______,_______,________
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK CONTROL SET POINTS
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK CRANKCASE HEATER
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK COMPRESSOR OIL LEVEL
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK LIQUID LINE SIGHT GLASS
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK MECHANICAL COOLING SEQUENCE OPERATION
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK INDOOR COIL
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | TEMPERATURE DROP #1________DEG.F #2_________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK COMPRESSOR DISCHARGE TEMPERATURE
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | #1__________DEG.F #2__________DEG.F
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK FOR REFRIGERANT LEAKS (VISUAL)
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK HOT GAS BYPASS OPERATION
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK CONDENSER WATER REGULATING VALVE
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | [ ] CHECK CONDENSER WATER TEMPERATURE
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | #1 IN_________OUT_________
WCCU | WATER COOLED CONDENSING UNIT | SUMMER | #2 IN_________OUT_________
WF | WATER FILTER | FALL | [ ] CHECK FOR WATER LEAKS
WF | WATER FILTER | FALL | [ ] CHECK FILTER PRESSURE DROP_______________
WF | WATER FILTER | WINTER | [ ] CHECK FOR WATER LEAKS
WF | WATER FILTER | WINTER | [ ] CHECK FILTER PRESSURE DROP___________________
WF | WATER FILTER | SPRING | [ ] CHECK FOR WATER LEAKS
WF | WATER FILTER | SPRING | [ ] CHECK FILTER PRESSURE DROP_______________
WF | WATER FILTER | SUMMER | [ ] CHECK FOR WATER LEAKS
WF | WATER FILTER | SUMMER | [ ] CHECK FILTER PRESSURE DROP________________
WH | WALL HEATER | FALL | [ ] CHECK THERMOSTAT
WH | WALL HEATER | FALL | [ ] CHECK FAN OPERATION
WH | WALL HEATER | FALL | [ ] CYCLE HEAT
WH | WALL HEATER | FALL | [ ] INSPECT BLOWER FOR DIRT
WH | WALL HEATER | FALL | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
WH | WALL HEATER | FALL | [ ] CHECK FOR FIRE HAZARDS
WH | WALL HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTION
WH | WALL HEATER | FALL | [ ] CHECK CONTACTOR POINTS
WH | WALL HEATER | WINTER | [ ] CHECK THERMOSTAT
WH | WALL HEATER | WINTER | [ ] CHECK FAN OPERATION
WH | WALL HEATER | WINTER | [ ] CYCLE HEAT
WH | WALL HEATER | WINTER | [ ] INSPECT BLOWER FOR DIRT
WH | WALL HEATER | WINTER | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
WH | WALL HEATER | WINTER | [ ] CHECK FOR FIRE HAZARDS
WH | WALL HEATER | SPRING | [ ] CHECK THERMOSTAT
WH | WALL HEATER | SPRING | [ ] CHECK FAN OPERATION
WH | WALL HEATER | SPRING | [ ] CYCLE HEAT
WH | WALL HEATER | SPRING | [ ] INSPECT BLOWER FOR DIRT
WH | WALL HEATER | SPRING | [ ] CHECK FOR UNUSUAL VIBRATION AND NOISE
WH | WALL HEATER | SPRING | [ ] CHECK FOR FIRE HAZARD
WH | WALL HEATER | SUMMER | [ ] CHECK THERMOSTATS
WH | WALL HEATER | SUMMER | [ ] CHECK FAN OPERATION
WH | WALL HEATER | SUMMER | [ ] CYCLE HEAT
WH | WALL HEATER | SUMMER | [ ] INSPECT BLOWER FOR DIRT
WH | WALL HEATER | SUMMER | [ ] CHECK FOR UNUSUAL VIBRATION OR NOISE
WH | WALL HEATER | SUMMER | [ ] CHECK FOR FIRE HAZARD
WHR | WATER HEATER | FALL | ELECTRIC WATER HEATER
WHR | WATER HEATER | FALL | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | FALL | [ ] CHECK OPERATION OF HEAT ELEMENTS
WHR | WATER HEATER | FALL | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
WHR | WATER HEATER | FALL | [ ] CHECK AMP DRAW_______________
WHR | WATER HEATER | FALL | [ ] CHECK VOLTAGE_________________
WHR | WATER HEATER | FALL | GAS WATER HEATER
WHR | WATER HEATER | FALL | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | FALL | [ ] CHECK BURNER OPERATION
WHR | WATER HEATER | FALL | [ ] INSPECT GAS BURNER
WHR | WATER HEATER | FALL | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | FALL | [ ] INSPECT FOR FIRE HAZARDS
WHR | WATER HEATER | WINTER | ELECTRIC WATER HEATER
WHR | WATER HEATER | WINTER | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | WINTER | [ ] CHECK OPERATION OF HEAT ELEMENTS
WHR | WATER HEATER | WINTER | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | WINTER | [ ] CHECK ELECTRICAL CONNECTIONS
WHR | WATER HEATER | WINTER | [ ] CHECK AMP DRAW____________
WHR | WATER HEATER | WINTER | [ ] CHECK VOLTAGE__________
WHR | WATER HEATER | WINTER | GAS WATER HEATER
WHR | WATER HEATER | WINTER | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | WINTER | [ ] CHECK BURNER OPERATION
WHR | WATER HEATER | WINTER | [ ] INSPECT GAS BURNER
WHR | WATER HEATER | WINTER | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | WINTER | [ ] INSPECT FOR FIRE HAZARD
WHR | WATER HEATER | SPRING | ELECTRIC WATER HEATER
WHR | WATER HEATER | SPRING | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | SPRING | [ ] CHECK OPERATION OF HEAT ELEMENTS
WHR | WATER HEATER | SPRING | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | SPRING | [ ] CHECK ELECTRICAL CONNECTIONS
WHR | WATER HEATER | SPRING | [ ] CHECK AMP DRAW_________________
WHR | WATER HEATER | SPRING | [ ] CHECK VOLTAGE________________
WHR | WATER HEATER | SPRING | GAS WATER HEATER
WHR | WATER HEATER | SPRING | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | SPRING | [ ] CHECK BURNER OPERATION
WHR | WATER HEATER | SPRING | [ ] INSPECT GAS BURNER
WHR | WATER HEATER | SPRING | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | SPRING | [ ] INSPECT FOR FIRE HAZARD
WHR | WATER HEATER | SUMMER | ELECTRIC WATER HEATER
WHR | WATER HEATER | SUMMER | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | SUMMER | [ ] CHECK OPERATION OF HEAT ELEMENTS
WHR | WATER HEATER | SUMMER | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | SUMMER | [ ] CHECK ELECTRICAL CONNECTIONS
WHR | WATER HEATER | SUMMER | [ ] CHECK AMP DRAW
WHR | WATER HEATER | SUMMER | [ ] CHECK VOLTAGE
WHR | WATER HEATER | SUMMER | GAS WATER HEATER
WHR | WATER HEATER | SUMMER | [ ] CHECK THERMOSTAT SETTING
WHR | WATER HEATER | SUMMER | [ ] CHECK BURNER OPERATION
WHR | WATER HEATER | SUMMER | [ ] INSPECT GAS BURNER
WHR | WATER HEATER | SUMMER | [ ] CHECK PRESSURE RELIEF
WHR | WATER HEATER | SUMMER | [ ] INSPECT FOR FIRE HAZARDS
WWP | WELL WATER PUMP | FALL | [ ] CHECK PRESSURE SETTING
WWP | WELL WATER PUMP | FALL | [ ] RECORD OPERATING PRESSURE______________
WWP | WELL WATER PUMP | FALL | [ ] CHECK VOLTAGE_________________
WWP | WELL WATER PUMP | FALL | [ ] CHECK AMP DRAW________________
WWP | WELL WATER PUMP | FALL | [ ] INSPECT FOR UNUSUAL VIBRATION AND NOISE
WWP | WELL WATER PUMP | FALL | [ ] INSPECT FOR WATER LEAKS
WWP | WELL WATER PUMP | FALL | [ ] CHECK ELECTRICAL CONNECTIONS
WWP | WELL WATER PUMP | FALL | [ ] CHECK CONTACTOR POINTS
WWP | WELL WATER PUMP | FALL | [ ] MEG OHM MOTOR (10 HP OR LARGER)
WWP | WELL WATER PUMP | FALL | [ ] LUBRICATE PUMP MOTOR (IF REQUIRED)
WWP | WELL WATER PUMP | FALL | [ ] CHECK STRAINER IF EQUIPPED
WWP | WELL WATER PUMP | WINTER | [ ] CHECK PRESSURE SETTING
WWP | WELL WATER PUMP | WINTER | [ ] RECORD OPERATING PRESSURE _______________
WWP | WELL WATER PUMP | WINTER | [ ] CHECK VOLTAGE_______________
WWP | WELL WATER PUMP | WINTER | [ ] CHECK AMP DRAW__________________
WWP | WELL WATER PUMP | WINTER | [ ] INSPECT FOR UNUSUAL VIBRATION AND NOISE
WWP | WELL WATER PUMP | WINTER | [ ] INSPECT FOR WATER LEAKS
WWP | WELL WATER PUMP | SPRING | [ ] CHECK PRESSURE SETTING
WWP | WELL WATER PUMP | SPRING | [ ] RECORD OPERATING PRESSURE__________________
WWP | WELL WATER PUMP | SPRING | [ ] CHECK VOLTAGE_____________________
WWP | WELL WATER PUMP | SPRING | [ ] CHECK AMP DRAW_____________________
WWP | WELL WATER PUMP | SPRING | [ ] INSPECT FOR UNUSUAL VIBRATION AND NOISE
WWP | WELL WATER PUMP | SPRING | [ ] INSPECT FOR WATER LEAKS
WWP | WELL WATER PUMP | SUMMER | [ ] CHECK PRESSURE SETTING
WWP | WELL WATER PUMP | SUMMER | [ ] RECORD OPERATING PRESSURE____________________
WWP | WELL WATER PUMP | SUMMER | [ ] CHECK VOLTAGE__________________
WWP | WELL WATER PUMP | SUMMER | [ ] CHECK AMP DRAW_________________
WWP | WELL WATER PUMP | SUMMER | [ ] INSPECT FOR UNUSUAL VIBRATION AND NOISE
WWP | WELL WATER PUMP | SUMMER | [ ] INSPECT FOR WATER LEAKS
[ ] CHANGE FILTERS